## FRA-detail
[6 empty] | UPRN | B7A4
High Rise flatted accomodation
Fire Risk Assessment (FRA)
Regulatory Reform (Fire Safety) Order 2005
473-77 (727) | Next review due on: |  | As FRA program
| Date of FRA: |  | 2017-06-30
| Responsible person (e.g. housing provider): |  |  | Chief Executive, Barnet Homes
| Fire Risk Assessor |  | The Fire Risk Assessment was undertaken by Mr Philip Holmes who has the necessary qualifications, competency and experience in Fire Risk Management that give him the status of “Competent Person” as described in articles 15 and 18 of the ‘Regulatory Reform (Fire Safety) Order 2005', for properties in England & Wales, and the 'Fire Safety (Scotland) Regulations 2006' for those in Scotland. This legislation now supersedes all previous fire legislation for England, Wales & Scotland and forms the ‘Fire Regulations'. He is an ex-fire enforcement officer by profession; has been trained through the Fire Service College in all necessary disciplines of fire safety, building design and building behaviour under fire conditions and is considered to be sufficiently practised in the necessary skills to enable him to carry out a practical fire risk assessment.
(include relevant professional memberships and/or qualifications)
Address of premises: | Person managing fire safety for the premises: |  |  | Health & Safety Manager
45-88 Upper Fosters, NW4 2DL
| Did you consult with any other individual during the FRA? |  |  |  | No
| If yes, provide | Name
Position within company
Barnet Homes UPRN: | Recommended review date: |  | The person managing fire safety should monitor the progress of work undertaken in rectifying the deficiencies reported and should ensure that checks are undertaken at target completion dates. A follow up inspection (taking the form of an interim fire risk assessment review) should be undertaken no more than one month from the time when the reported ‘Priority P0’ deficiencies have been identified and additionally in six months by which time Priority P1 deficiencies should have been actioned. It is Barnet Homes policy that a review of the fire risk assessment will be undertaken no later than 12 months from the date of inspection.
B7A4
Euro Compliance Limited
Company Reg. No. 6353434
Members of the Institute of Fire Engineers
Yes
No

## Premises summary
[6 empty] | UPRN | B7A4
Premises: | 45-88 Upper Fosters, NW4 2DL |  |  | FRA undertaken on (date): | 2017-06-30
Risk rating | Moderate | Risk rating legend | [5 empty] | Trivial
| The works listed in this report (Action Plan) are recommended to reduce the level of risk to (or maintain it at) Tolerable | [6 empty] | Tolerable
Moderate
Extent of common areas | [7 empty] | Substantial
Internal and external communal areas including the following: entrances, exits, escape stairs, landings, lobbies, electrical intake/service cupboards, pram shed areas, refuse areas. Ventilation-opening windows | [7 empty] | Intolerable
Details of building construction (approx. age, structure, cladding, walls, roof)
Purpose built concrete frame with flat roof, high rise residential block. |  | Low | Unusually low likelihood of fire as a result of negligible potential sources of ignition.
|  | Medium | Normal fire hazards (e.g. potential ignition sources) for this type of occupancy, with fire hazards generally subject to appropriate controls (other than minor shortcomings).
|  | High | Lack of adequate controls applied to one or more significant fire hazards, such as to result in significant increases in likelihood of fire.
|  | Slight harm | Outbreak of fire unlikely to result in serious injury or death of any occupant (other than an occupant sleeping in a room in which a fire occurs).
Details of building layout (number of flats, floors, staircases, lifts, etc.) |  | Moderate harm | Outbreak of fire could foreseeably result in injury (including serious injury) of one or more occupants, but it is unlikely to involve multiple fatalities.
44 flats, 11 floors, 2 staircase and 2 lifts (not FF).
|  | Extreme harm | Significant potential for serious injury or death of one or more occupants.
|  | Risk level | Action and timescale
|  | Trivial | No action is required and no detailed records need be kept.
|  | Tolerable | No major additional controls required. However, there might be a need for improvements that involve minor or limited cost.
How are occupants who warrant special consideration identified? |  | Moderate | It is essential that efforts are made to reduce the risk. Risk reduction measures should be implemented within a defined time period. Where moderate risk is associated with consequences that constitute extreme harm, further assessment might be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures.
In the event of an emergency vulnerability is obtained from the OHMS database available to the Barnet Homes Emergency Officer
|  | Substantial | Considerable resources might have to be allocated to reduce the risk. If the building is unoccupied it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken.
Any other relevant information (including previous fire loss experience)
Barnet Homes Fire Policy and Procedure document forms part of the organisations' Health & Safety Policy and is reviewed by the Board on an annual basis.
|  | Intolerable | Building (or relevant areas) should not be occupied until the risk is reduced.
Areas where access was not available

## FRA
Priority | Description | Timescale |  |  | Over-All Block Risk Rating |  | UPRN | B7A4
P0 | When an unacceptable risk to fire safety is present. (Works typically carried out by Housing/Repairs) | Within 10 days |  |  | Any |  |  |  |  | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the Note - RESPONSIVE REPAIRS TEAM | Within 6 months |  |  | Any |  |  |  |  | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year |  |  | Substantial |  |  |  |  | n/k | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years |  |  | Moderate |  |  |  |  | n/a | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years |  |  | Tolerable | [5 empty] | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural |  |  | Ongoing | [5 empty] | FRA Team
Premises: | 45-88 Upper Fosters, NW4 2DL |  |  | FRA undertaken on (date): | 2017-06-30
FIRE RISK ASSESSMENT
Question | Fire safety measures | Yes/No n/k-n/a | Priority | Location and comment | Ownership | Details | Ongoing from last FRA? | Completed date
Hazard identification - housekeeping | [8 empty] | 0
1 | Are combustibles separated from ignition sources? | Yes | [6 empty] | 0
1 | [8 empty] | 0
2 | Is unnecessary storage of combustible materials/waste avoided? | No | P0 | Remove the combustible storage from the intake (paint and thinners) |  |  |  |  | 1
2 | [8 empty] | 1
3 | Are hazardous materials stored appropriately? | n/a | [6 empty] | 1
Hazard identification - arson | [8 empty] | 1
4 | Are premises secure against arson by outsiders? | No | P3 | There is a secure entry system fitted to this block however it is defective and requires repair |  |  |  |  | 2
4 | [8 empty] | 2
5 | Are bins secured and stored in a suitable location? | Yes |  | The bins are secured and remote. |  |  |  |  | 2
5 | [8 empty] | 2
6 | Is fire load close to the premises minimised? | Yes |  | No evidence of fire loads near premises. |  |  |  |  | 2
6 | [8 empty] | 2
Hazard identification - smoking | [8 empty] | 2
7 | Smoking in inappropriate places. | No | [6 empty] | 2
7 | [8 empty] | 2
Hazard identification - any other issues - specify | [8 empty] | 2
8 | Is loft hatch secured | n/a | [6 empty] | 2
8 | [8 empty] | 2
Means of escape | [8 empty] | 2
9 | Is escape route design satisfactory? (see Home Office guides) | Yes |  | The escape stairs are satisfactory for the number of persons expected in the building at any given time |  |  |  |  | 2
9 | [8 empty] | 2
10 | Are escape routes clear and unobstructed? | Yes | [6 empty] | 2
10 | [8 empty] | 2
11 | Is number and provision of exits adequate? | Yes |  | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. |  |  |  |  | 2
11 | [8 empty] | 2
12 | Are doors on escape routes easily opened? | Yes | [6 empty] | 2
12 | [8 empty] | 2
13 | Are travel distances satisfactory - single and two-way? | Yes |  | The travel distances are satisfactory as per the recommendations in Approved Document B |  |  |  |  | 2
13 | [8 empty] | 2
14 | Are escape routes adequately protected? Consider: storage and electrical cupboards, refuse chutes, fire doors (incl. provision, location, self-closers, strips and seals, condition), stair ventilation | No | P3 | All staircase doors require smoke seals as a minimum, however it is recommended that all staircase doors are replaced with certified FD30S doors fitted to BS8214 |  |  |  |  | 3
14 |  | No | P3 | The electrical intake cupboard door is not a fire rated door and it is recommended that it is replaced with an FD30S door fitted in accordance to BS8214 in any future works improvement program, this includes all X 11 EIC riser doors. Main intake secured by FB2 all risers not secure and should be kept locked |  |  |  |  | 4
14 |  |  |  | FED 45 checked in the open position |  |  |  |  | 4
14 |  | No | P3 | Bin chute hoppers require service/maintenance on all floors and confirmation of fusible link in the bin room required |  |  |  |  | 5
14 |  | No | P3 | All flat entrance doors in this block (except for flats, 54, 64 and 76) appear to be notional FD30S doors and they appear to have been upgraded. However, they are not FD30S doors to current standard and should be replaced with certified FD30S doorsets which should be fitted in accordance to BS8214. |  |  |  |  | 6
14 |  | No | P3 | All compartment breaches in the intakes should be fire stopped using appropriate materials |  |  |  |  | 7
14 |  |  |  | Last EIC 07/12 |  |  |  |  | 7
14 |  | No | P3 | Repair holes in walls above flat 50 and above ground and 1st floor riser cupboards |  |  |  |  | 8
14 |  | No | P3 | Riser protection on the ground floor by the bin chute is defective and requires repair |  |  |  |  | 9
14 | [8 empty] | 9
15 | Are escape routes separated (where appropriate)? | Yes | [6 empty] | 9
15 | [8 empty] | 9
16 | Do escape routes lead to a place of safety? | Yes |  | All escape routes lead to open air at ground level. |  |  |  |  | 9
16 | [8 empty] | 9
17 | Are corridors sub-divided (where appropriate)? | Yes | [6 empty] | 9
17 | [8 empty] | 9
18 | Are floors free from slipping/tripping hazards? | No | P3 | There are pholuminescent stair nosings fitted but they are not to the correct size and these should be replaced in any future works program. There are also missing treads on steps 8, 9 and 38 which should be replaced. |  |  |  |  | 10
18 | [8 empty] | 10
19 | Is it considered that the building is provided with reasonable arrangements for means of escape of disabled people? | No |  | All stair nosings should be easily identifiable to visually impaired and blind persons as a matter of duty of care and should achieve the Light Reflectance Values as set out in ADM (a LRV of 30). |  |  |  |  | 10
19 | [8 empty] | 10
Emergency escape lighting | [8 empty] | 10
20 | Is emergency escape lighting coverage sufficient (internal and external)? | Yes | P3 | Non-maintained emergency lighting is fitted in this building, however it has not been fitted to BS5266-1 and should be reconfigured/reinstalled to meet the design specifications detailed in BS5266-1. Alternatively, consideration should be given to fitting a Photoluminescent low level wayguidance system (PSPA Class D) in accordance with BS5266 part 6. |  |  |  |  | 11
20 | [8 empty] | 11
21 | Is emergency escape lighting in good working order? | n/k |  | It appears to be but please see Q.20, also no test dates on the premises |  |  |  |  | 11
21 | [8 empty] | 11
Signage | [8 empty] | 11
22 | Is there adequate provision of fire safety signs and notices? | No | P3 | Floor ID signage (floor numbers) required to all floors (staircase and lobbies). A full fire safety signage survey should be carried out |  |  |  |  | 12
22 | [8 empty] | 12
22 | [8 empty] | 12
22 | [8 empty] | 12
22 | [8 empty] | 12
22 | [8 empty] | 12
23 | Are signs clearly visible and not obstructed? | No | [6 empty] | 12
23 | [8 empty] | 12
Fire detection and alarm | [8 empty] | 12
24 | Is automatic detection and/or manual alarm provided in the premises? If yes, describe system. | n/k | [6 empty] | 12
24 | [8 empty] | 12
25 | Is further automatic detection and/or manual alarm provision required? If yes, state what. | n/k | P3 | It would be advisable to fit a BS5839-6 LD2 system to all flats if not already fitted. Review recommended. |  |  |  |  | 13
25 | [8 empty] | 13
26 | Is the fire alarm system in working order? | n/a | [6 empty] | 13
26 | [8 empty] | 13
Limiting fire spread | [8 empty] | 13
27 | Is the level of compartmentation adequate? (Special consideration should be given to converted or non 'purpose built' premises.) | n/k | P3 | The building has internal stacks and therefore we would recommend that a sample survey of 2 or more flats is carried out to ensure that the compartmentation levels between flats is adequate as well as to communal areas. |  |  |  |  | 14
27 | [8 empty] | 14
27 | [8 empty] | 14
27 | [8 empty] | 14
27 | [8 empty] | 14
28 | Are linings appropriate to limit fire spread? | No | P3 | There is paint delamination throughout this building which should be removed and redecorated with Class 0 materials/paint |  |  |  |  | 15
28 | [8 empty] | 15
29 | Where required, are dampers provided? | n/a | [6 empty] | 15
29 | [8 empty] | 15
Fire fighting equipment | [8 empty] | 15
30 | Provision, accessibility and condition of portable fire extinguishers | n/a | [6 empty] | 15
30 | [8 empty] | 15
31 | Provision and condition of other fire extinguishing systems | n/a | [6 empty] | 15
31 | [8 empty] | 15
32 | Are dry/wet risers in good order? | Yes | P3 | However some of the DRM outlets are fixed at acute angles which would make it difficult for the fire service to couple hoses. It is recommended that these are replaced with 90 degree outlet valves. (QA check required). Last recorded test/check date 12/16 |  |  |  |  | 16
32 | [8 empty] | 16
33 | Is fireman's switch working correctly? | Yes | [6 empty] | 16
33 | [8 empty] | 16
Other issues | [8 empty] | 16
34 | Electrical intake/s checked? | Yes | P3 | The main electric intake doors were secure and there was no storage. There are no compartment breaches in the EIC's. All EIC doors are not FD30S standard and should be replaced with FD30S doors which should be fitted in accordance to BS8214. Unable to access EIC on the 3rd floor. Electrics last tested 20/6/12 |  |  |  |  | 17
35 | Internal stacks? | Yes | P3 | Soil stacks are internal and it is recommended that an internal flat survey is carried out to determine the level of compartmentation from flat to flat as well as to the communal space. Due to the building layout, we would recommend surveys of at least 2 flats, in different parts of the building. |  |  |  |  | 18
36 | External cladding | Yes | P1 | There is external cladding fitted to this building and it is recommended that it is tested to determine its level of combustibility |  |  |  |  | 19
37 | [8 empty] | 19

## M-M
Priority | Description | Timescale |  |  |  |  | UPRN | B7A4
P0 | When an unacceptable risk to fire safety is present. Works typically carried out by Housing/Repairs | Within 10 days | [7 empty] | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the RESPONSIVE REPAIRS TEAM | Within 6 months | [7 empty] | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year | [7 empty] | n/a | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years | [8 empty] | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years | [8 empty] | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/ procedural | [8 empty] | FRA Team
Premises: | 45-88 Upper Fosters, NW4 2DL |  |  | FRA undertaken on (date): | 2017-06-30
Management/maintenance
Question | Management/maintenance | Yes/ No/ n/a | Priority | Location and comment | Ownership | Details | Ongoing from last FRA? | Completed date
Premises management | [8 empty] | 19
38 | Is there a suitable record of fire safety arrangements available? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  |  | 19
38 | [8 empty] | 19
39 | Are appropriate fire safety procedures in place? Consider: Emergency action plans; calling/meeting the fire service; ensuring the premises are evacuated; assembly points; assistance for disabled; information to external contractors; nominated staff duties | Yes |  | All responsibilities for fire safety have been addressed with Barnet Homes Fire Safety Policy. The policy is available to all staff on the company intranet. |  |  |  |  | 19
39 | [8 empty] | 19
40 | Has any liaison taken place with the local fire and rescue service? | Yes |  | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. |  |  |  |  | 19
40 | [8 empty] | 19
Training | [8 empty] | 19
41 | Do staff receive induction and/or annual fire safety refresher training? | Yes |  | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. |  |  |  |  | 19
41 | [8 empty] | 19
42 | If drills are considered appropriate, are they carried out at regular intervals? | n/a | [6 empty] | 19
42 | [8 empty] | 19
Maintenance checks | [8 empty] | 19
43 | Are the premises generally well maintained? | Yes |  | The building is generally well maintained with some minor defects that form part of the action plan |  |  |  |  | 19
43 | [8 empty] | 19
44 | Do appropriate regular checks take place? | Yes |  | Regular checks of the premises are carried out and any defects reported to the building maintenance office. |  |  |  |  | 19
44 | [8 empty] | 19
45 | Is the alarm system adequately maintained? | n/a | [6 empty] | 19
45 | [8 empty] | 19
46 | Is the escape lighting adequately maintained? | No | P4 | No emergency lighting test dates on the premises. Check emergency lighting test records |  |  |  |  | 20
46 | [8 empty] | 20
47 | Are fire extinguishers adequately maintained? | n/a | [6 empty] | 20
47 | [8 empty] | 20
48 | Are rising mains adequately maintained? | Yes | [6 empty] | 20
48 | [8 empty] | 20
49 | Are fireman lifts adequately maintained? | n/a | [6 empty] | 20
49 | [8 empty] | 20
50 | Is the sprinkler system adequately maintained? | n/a | [6 empty] | 20
50 | [8 empty] | 20
51 | Is the lightning protection system adequately maintained? | Yes |  | A schedule of maintenance is completed by Technical Services under a Service Level Agreement (SLA) |  |  |  |  | 20
51 | [8 empty] | 20
Records | [8 empty] | 20
52 | Are fire safety maintenance records available for the premises? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  |  | 20
52 | [8 empty] | 20
53 | Are fire drills recorded? | n/a | [6 empty] | 20
53 | [8 empty] | 20
54 | Is fire safety training recorded? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  |  | 20
54 | [8 empty] | 20
55 | Are fire alarm tests recorded? | n/a | [6 empty] | 20
55 | [8 empty] | 20
56 | Are emergency escape lighting tests recorded? | Yes |  | It is believed that emergency lighting test records are kept centrally by Barnet Homes |  |  |  |  | 20
56 | [8 empty] | 20
Other issues | [8 empty] | 20
57 | [8 empty] | 20
58 | [8 empty] | 20
59 | [8 empty] | 20
60 | [8 empty] | 20
61 | [8 empty] | 20
62 | [8 empty] | 20

## ActionPlan
[5 empty] | UPRN | B7A4
| Priority | Description | Timescale |  |  |  | No
| P0 | When an unacceptable risk to fire safety is present. Works typically carried out by Housing/Repairs | Within 10 days |  |  |  | n/a
| P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the RESPONSIVE REPAIRS TEAM | Within 6 months
| P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year
| P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years |  | Fire Risk Assessment Action Plan
| P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years
| P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/ procedural
| Premises: | 45-88 Upper Fosters, NW4 2DL |  |  | FRA undertaken on (date): | 2017-06-30
| Question | Action to be taken | Priority | Ownership | Details | Ongoing from last FRA
1 | 2 | Remove the combustible storage from the intake (paint and thinners) | P0
2 | 4 | There is a secure entry system fitted to this block however it is defective and requires repair | P3
3 | 14 | All staircase doors require smoke seals as a minimum, however it is recommended that all staircase doors are replaced with certified FD30S doors fitted to BS8214 | P3
4 | 14 | The electrical intake cupboard door is not a fire rated door and it is recommended that it is replaced with an FD30S door fitted in accordance to BS8214 in any future works improvement program, this includes all X 11 EIC riser doors. Main intake secured by FB2 all risers not secure and should be kept locked | P3
5 | 14 | Bin chute hoppers require service/maintenance on all floors and confirmation of fusible link in the bin room required | P3
6 | 14 | All flat entrance doors in this block (except for flats, 54, 64 and 76) appear to be notional FD30S doors and they appear to have been upgraded. However, they are not FD30S doors to current standard and should be replaced with certified FD30S doorsets which should be fitted in accordance to BS8214. | P3
7 | 14 | All compartment breaches in the intakes should be fire stopped using appropriate materials | P3
8 | 14 | Repair holes in walls above flat 50 and above ground and 1st floor riser cupboards | P3
9 | 14 | Riser protection on the ground floor by the bin chute is defective and requires repair | P3
10 | 18 | There are pholuminescent stair nosings fitted but they are not to the correct size and these should be replaced in any future works program. There are also missing treads on steps 8, 9 and 38 which should be replaced. | P3
11 | 20 | Non-maintained emergency lighting is fitted in this building, however it has not been fitted to BS5266-1 and should be reconfigured/reinstalled to meet the design specifications detailed in BS5266-1. Alternatively, consideration should be given to fitting a Photoluminescent low level wayguidance system (PSPA Class D) in accordance with BS5266 part 6. | P3
12 | 22 | Floor ID signage (floor numbers) required to all floors (staircase and lobbies). A full fire safety signage survey should be carried out | P3
13 | 25 | It would be advisable to fit a BS5839-6 LD2 system to all flats if not already fitted. Review recommended. | P3
14 | 27 | The building has internal stacks and therefore we would recommend that a sample survey of 2 or more flats is carried out to ensure that the compartmentation levels between flats is adequate as well as to communal areas. | P3
15 | 28 | There is paint delamination throughout this building which should be removed and redecorated with Class 0 materials/paint | P3
16 | 32 | However some of the DRM outlets are fixed at acute angles which would make it difficult for the fire service to couple hoses. It is recommended that these are replaced with 90 degree outlet valves. (QA check required). Last recorded test/check date 12/16 | P3
17 | 34 | The main electric intake doors were secure and there was no storage. There are no compartment breaches in the EIC's. All EIC doors are not FD30S standard and should be replaced with FD30S doors which should be fitted in accordance to BS8214. Unable to access EIC on the 3rd floor. Electrics last tested 20/6/12 | P3
18 | 35 | Soil stacks are internal and it is recommended that an internal flat survey is carried out to determine the level of compartmentation from flat to flat as well as to the communal space. Due to the building layout, we would recommend surveys of at least 2 flats, in different parts of the building. | P3
19 | 36 | There is external cladding fitted to this building and it is recommended that it is tested to determine its level of combustibility | P1
20 | 46 | No emergency lighting test dates on the premises. Check emergency lighting test records | P4
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63

## Data (hidden)
KeyID | Question | Priority | Location and comment | Ownership | Details | Ongoing from last FRA
0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 1 | 0 | 0 | 0 | 0 | 0
1 | 2 | P0 | Remove the combustible storage from the intake (paint and thinners) | 0 | 0 | 0
1 | 2 | 0 | 0 | 0 | 0 | 0
1 | 3 | 0 | 0 | 0 | 0 | 0
1 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | P3 | There is a secure entry system fitted to this block however it is defective and requires repair | 0 | 0 | 0
2 | 4 | 0 | 0 | 0 | 0 | 0
2 | 5 | 0 | The bins are secured and remote. | 0 | 0 | 0
2 | 5 | 0 | 0 | 0 | 0 | 0
2 | 6 | 0 | No evidence of fire loads near premises. | 0 | 0 | 0
2 | 6 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 0 | 0 | 0 | 0 | 0
2 | 7 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 0 | 0 | 0 | 0 | 0
2 | 8 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 0 | The escape stairs are satisfactory for the number of persons expected in the building at any given time | 0 | 0 | 0
2 | 9 | 0 | 0 | 0 | 0 | 0
2 | 10 | 0 | 0 | 0 | 0 | 0
2 | 10 | 0 | 0 | 0 | 0 | 0
2 | 11 | 0 | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. | 0 | 0 | 0
2 | 11 | 0 | 0 | 0 | 0 | 0
2 | 12 | 0 | 0 | 0 | 0 | 0
2 | 12 | 0 | 0 | 0 | 0 | 0
2 | 13 | 0 | The travel distances are satisfactory as per the recommendations in Approved Document B | 0 | 0 | 0
2 | 13 | 0 | 0 | 0 | 0 | 0
3 | 14 | P3 | All staircase doors require smoke seals as a minimum, however it is recommended that all staircase doors are replaced with certified FD30S doors fitted to BS8214 | 0 | 0 | 0
4 | 14 | P3 | The electrical intake cupboard door is not a fire rated door and it is recommended that it is replaced with an FD30S door fitted in accordance to BS8214 in any future works improvement program, this includes all X 11 EIC riser doors. Main intake secured by FB2 all risers not secure and should be kept locked | 0 | 0 | 0
4 | 14 | 0 | FED 45 checked in the open position | 0 | 0 | 0
5 | 14 | P3 | Bin chute hoppers require service/maintenance on all floors and confirmation of fusible link in the bin room required | 0 | 0 | 0
6 | 14 | P3 | All flat entrance doors in this block (except for flats, 54, 64 and 76) appear to be notional FD30S doors and they appear to have been upgraded. However, they are not FD30S doors to current standard and should be replaced with certified FD30S doorsets which should be fitted in accordance to BS8214. | 0 | 0 | 0
7 | 14 | P3 | All compartment breaches in the intakes should be fire stopped using appropriate materials | 0 | 0 | 0
7 | 14 | 0 | Last EIC 07/12 | 0 | 0 | 0
8 | 14 | P3 | Repair holes in walls above flat 50 and above ground and 1st floor riser cupboards | 0 | 0 | 0
9 | 14 | P3 | Riser protection on the ground floor by the bin chute is defective and requires repair | 0 | 0 | 0
9 | 14 | 0 | 0 | 0 | 0 | 0
9 | 15 | 0 | 0 | 0 | 0 | 0
9 | 15 | 0 | 0 | 0 | 0 | 0
9 | 16 | 0 | All escape routes lead to open air at ground level. | 0 | 0 | 0
9 | 16 | 0 | 0 | 0 | 0 | 0
9 | 17 | 0 | 0 | 0 | 0 | 0
9 | 17 | 0 | 0 | 0 | 0 | 0
10 | 18 | P3 | There are pholuminescent stair nosings fitted but they are not to the correct size and these should be replaced in any future works program. There are also missing treads on steps 8, 9 and 38 which should be replaced. | 0 | 0 | 0
10 | 18 | 0 | 0 | 0 | 0 | 0
10 | 19 | 0 | All stair nosings should be easily identifiable to visually impaired and blind persons as a matter of duty of care and should achieve the Light Reflectance Values as set out in ADM (a LRV of 30). | 0 | 0 | 0
10 | 19 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | P3 | Non-maintained emergency lighting is fitted in this building, however it has not been fitted to BS5266-1 and should be reconfigured/reinstalled to meet the design specifications detailed in BS5266-1. Alternatively, consideration should be given to fitting a Photoluminescent low level wayguidance system (PSPA Class D) in accordance with BS5266 part 6. | 0 | 0 | 0
11 | 20 | 0 | 0 | 0 | 0 | 0
11 | 21 | 0 | It appears to be but please see Q.20, also no test dates on the premises | 0 | 0 | 0
11 | 21 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | P3 | Floor ID signage (floor numbers) required to all floors (staircase and lobbies). A full fire safety signage survey should be carried out | 0 | 0 | 0
12 | 22 | 0 | 0 | 0 | 0 | 0
12 | 22 | 0 | 0 | 0 | 0 | 0
12 | 22 | 0 | 0 | 0 | 0 | 0
12 | 22 | 0 | 0 | 0 | 0 | 0
12 | 22 | 0 | 0 | 0 | 0 | 0
12 | 23 | 0 | 0 | 0 | 0 | 0
12 | 23 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 0 | 0 | 0 | 0 | 0
12 | 24 | 0 | 0 | 0 | 0 | 0
13 | 25 | P3 | It would be advisable to fit a BS5839-6 LD2 system to all flats if not already fitted. Review recommended. | 0 | 0 | 0
13 | 25 | 0 | 0 | 0 | 0 | 0
13 | 26 | 0 | 0 | 0 | 0 | 0
13 | 26 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0
14 | 27 | P3 | The building has internal stacks and therefore we would recommend that a sample survey of 2 or more flats is carried out to ensure that the compartmentation levels between flats is adequate as well as to communal areas. | 0 | 0 | 0
14 | 27 | 0 | 0 | 0 | 0 | 0
14 | 27 | 0 | 0 | 0 | 0 | 0
14 | 27 | 0 | 0 | 0 | 0 | 0
14 | 27 | 0 | 0 | 0 | 0 | 0
15 | 28 | P3 | There is paint delamination throughout this building which should be removed and redecorated with Class 0 materials/paint | 0 | 0 | 0
15 | 28 | 0 | 0 | 0 | 0 | 0
15 | 29 | 0 | 0 | 0 | 0 | 0
15 | 29 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0
15 | 30 | 0 | 0 | 0 | 0 | 0
15 | 30 | 0 | 0 | 0 | 0 | 0
15 | 31 | 0 | 0 | 0 | 0 | 0
15 | 31 | 0 | 0 | 0 | 0 | 0
16 | 32 | P3 | However some of the DRM outlets are fixed at acute angles which would make it difficult for the fire service to couple hoses. It is recommended that these are replaced with 90 degree outlet valves. (QA check required). Last recorded test/check date 12/16 | 0 | 0 | 0
16 | 32 | 0 | 0 | 0 | 0 | 0
16 | 33 | 0 | 0 | 0 | 0 | 0
16 | 33 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0
17 | 34 | P3 | The main electric intake doors were secure and there was no storage. There are no compartment breaches in the EIC's. All EIC doors are not FD30S standard and should be replaced with FD30S doors which should be fitted in accordance to BS8214. Unable to access EIC on the 3rd floor. Electrics last tested 20/6/12 | 0 | 0 | 0
18 | 35 | P3 | Soil stacks are internal and it is recommended that an internal flat survey is carried out to determine the level of compartmentation from flat to flat as well as to the communal space. Due to the building layout, we would recommend surveys of at least 2 flats, in different parts of the building. | 0 | 0 | 0
19 | 36 | P1 | There is external cladding fitted to this building and it is recommended that it is tested to determine its level of combustibility | 0 | 0 | 0
19 | 37 | 0 | 0 | 0 | 0 | 0
19 | 38 | 0 | Records are held centrally by the Health and Safety Team | 0 | 0 | 0
19 | 38 | 0 | 0 | 0 | 0 | 0
19 | 39 | 0 | All responsibilities for fire safety have been addressed with Barnet Homes Fire Safety Policy. The policy is available to all staff on the company intranet. | 0 | 0 | 0
19 | 39 | 0 | 0 | 0 | 0 | 0
19 | 40 | 0 | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. | 0 | 0 | 0
19 | 40 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0
19 | 41 | 0 | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. | 0 | 0 | 0
19 | 41 | 0 | 0 | 0 | 0 | 0
19 | 42 | 0 | 0 | 0 | 0 | 0
19 | 42 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0
19 | 43 | 0 | The building is generally well maintained with some minor defects that form part of the action plan | 0 | 0 | 0
19 | 43 | 0 | 0 | 0 | 0 | 0
19 | 44 | 0 | Regular checks of the premises are carried out and any defects reported to the building maintenance office. | 0 | 0 | 0
19 | 44 | 0 | 0 | 0 | 0 | 0
19 | 45 | 0 | 0 | 0 | 0 | 0
19 | 45 | 0 | 0 | 0 | 0 | 0
20 | 46 | P4 | No emergency lighting test dates on the premises. Check emergency lighting test records | 0 | 0 | 0
20 | 46 | 0 | 0 | 0 | 0 | 0
20 | 47 | 0 | 0 | 0 | 0 | 0
20 | 47 | 0 | 0 | 0 | 0 | 0
20 | 48 | 0 | 0 | 0 | 0 | 0
20 | 48 | 0 | 0 | 0 | 0 | 0
20 | 49 | 0 | 0 | 0 | 0 | 0
20 | 49 | 0 | 0 | 0 | 0 | 0
20 | 50 | 0 | 0 | 0 | 0 | 0
20 | 50 | 0 | 0 | 0 | 0 | 0
20 | 51 | 0 | A schedule of maintenance is completed by Technical Services under a Service Level Agreement (SLA) | 0 | 0 | 0
20 | 51 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0
20 | 52 | 0 | Records are held centrally by the Health and Safety Team | 0 | 0 | 0
20 | 52 | 0 | 0 | 0 | 0 | 0
20 | 53 | 0 | 0 | 0 | 0 | 0
20 | 53 | 0 | 0 | 0 | 0 | 0
20 | 54 | 0 | Records are held centrally by the Health and Safety Team | 0 | 0 | 0
20 | 54 | 0 | 0 | 0 | 0 | 0
20 | 55 | 0 | 0 | 0 | 0 | 0
20 | 55 | 0 | 0 | 0 | 0 | 0
20 | 56 | 0 | It is believed that emergency lighting test records are kept centrally by Barnet Homes | 0 | 0 | 0
20 | 56 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0
20 | 57 | 0 | 0 | 0 | 0 | 0
20 | 58 | 0 | 0 | 0 | 0 | 0
20 | 59 | 0 | 0 | 0 | 0 | 0
20 | 60 | 0 | 0 | 0 | 0 | 0
20 | 61 | 0 | 0 | 0 | 0 | 0
20 | 62 | 0 | 0 | 0 | 0 | 0