## FRA-detail
[6 empty] | UPRN | B132A26
General needs flatted accommodation
Fire Risk Assessment (FRA)
Regulatory Reform (Fire Safety) Order 2005
857-871 | Next review due on: |  | As per FRA program
| Date of FRA: |  | 2017-03-30
| Responsible person (e.g. housing provider): |  |  | Chief Executive, Barnet Homes
| Fire Risk Assessor |  | The Fire Risk Assessment was undertaken by Mr Haddon McLean who has the necessary qualifications, competency and experience in Fire Risk Management that give him the status of “Competent Person” as described in articles 15 and 18 of the ‘Regulatory Reform (Fire Safety) Order 2005', for properties in England & Wales, and the 'Fire Safety (Scotland) Regulations 2006' for those in Scotland. This legislation now supersedes all previous fire legislation for England, Wales & Scotland and forms the ‘Fire Regulations'. He is an ex-fire enforcement officer by profession; has been trained through the Fire Service College in all necessary disciplines of fire safety, building design and building behaviour under fire conditions and is considered to be sufficiently practised in the necessary skills to enable him to carry out a practical fire risk assessment.
(relevant professional memberships & qualifications)
Address of premises: | Person managing fire safety for the premises: |  |  | Health & Safety Manager
Hudson 1-45, NW9 5YL (
| Did you consult with any other individual during the FRA? |  |  |  | No
| If yes, provide | Name
Position within company
Barnet Homes UPRN: | Recommended review date: |  | The person managing fire safety should monitor the progress of work undertaken in rectifying the deficiencies reported and should ensure that checks are undertaken at target completion dates. A follow up inspection (taking the form of an interim fire risk assessment review) should be undertaken no more than one month from the time when the reported ‘Priority P0’ deficiencies have been identified and additionally in six months by which time Priority P1 deficiencies should have been actioned. It is Barnet Homes policy that a review of the fire risk assessment will be undertaken no later than 12 months from the date of inspection.
Euro Compliance Limited
Institute of Fire Engineers
Company Reg. No. 6353435
Yes
No

## Premises summary
[6 empty] | UPRN | B132A26
Premises: | Hudson 1-45, NW9 5YL ( |  |  | FRA undertaken on (date): | 2017-03-30
Risk rating | Moderate | Risk rating legend | [5 empty] | Trivial
| The works listed in this report (Action Plan) are recommended to reduce the level of risk to (or maintain it at) Tolerable | [6 empty] | Tolerable
Moderate
Extent of common areas | [7 empty] | Substantial
Internal and external communal areas including the following: entrances, exits, escape stairs, landings, lobbies, electrical intake/service cupboards, pram shed areas, refuse areas. Ventilation-open balcony | [7 empty] | Intolerable
Details of building construction (approx. age, structure, cladding, walls, roof)
Concrete frame with brick walls and pitched roof |  | Low | Unusually low likelihood of fire as a result of negligible potential sources of ignition.
|  | Medium | Normal fire hazards (e.g. potential ignition sources) for this type of occupancy, with fire hazards generally subject to appropriate controls (other than minor shortcomings).
|  | High | Lack of adequate controls applied to one or more significant fire hazards, such as to result in significant increases in likelihood of fire.
|  | Slight harm | Outbreak of fire unlikely to result in serious injury or death of any occupant (other than an occupant sleeping in a room in which a fire occurs).
Details of building layout (number of flats, floors, staircases, lifts, etc.) |  | Moderate harm | Outbreak of fire could foreseeably result in injury (including serious injury) of one or more occupants, but it is unlikely to involve multiple fatalities.
45 flats, 4 and 6 floors, 3 staircases and 2 lifts.
|  | Extreme harm | Significant potential for serious injury or death of one or more occupants.
|  | Risk level | Action and timescale
|  | Trivial | No action is required and no detailed records need be kept.
|  | Tolerable | No major additional controls required. However, there might be a need for improvements that involve minor or limited cost.
How are occupants who warrant special consideration identified? |  | Moderate | It is essential that efforts are made to reduce the risk. Risk reduction measures should be implemented within a defined time period. Where moderate risk is associated with consequences that constitute extreme harm, further assessment might be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures.
In the event of an emergency vulnerability is obtained from the OHMS database available to the Barnet Homes Emergency Officer
|  | Substantial | Considerable resources might have to be allocated to reduce the risk. If the building is unoccupied it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken.
Any other relevant information (including previous fire loss experience)
Barnet Homes Fire Policy and Procedure document forms part of the organisations' Health & Safety Policy and is reviewed by the Board on an annual basis.
|  | Intolerable | Building (or relevant areas) should not be occupied until the risk is reduced.
Areas where access was not available
roof void

## FRA
Priority | Description | Timescale |  |  | Over-All Block Risk Rating |  | UPRN | B132A26
P0 | When an unacceptable risk to fire safety is present. (Works typically carried out by Housing/Repairs) | Within 10 days |  |  | Any |  |  |  |  | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the Note - RESPONSIVE REPAIRS TEAM | Within 6 months |  |  | Any |  |  |  |  | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year |  |  | Substantial |  |  |  |  | n/k | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years |  |  | Moderate |  |  |  |  | n/a | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years |  |  | Tolerable | [5 empty] | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural |  |  | Ongoing | [5 empty] | FRA Team
Premises: | Hudson 1-45, NW9 5YL ( |  |  | FRA undertaken on (date): | 2017-03-30
Question | Fire safety measures | Yes/No n/k-n/a | Priority | Location and comment | Ownership | Details | Ongoing from last FRA? | Completed date
Hazard identification - housekeeping | [8 empty] | 0
1 | Are combustibles separated from ignition sources? | Yes | [6 empty] | 0
1 | [8 empty] | 0
2 | Is unnecessary storage of combustible materials/waste avoided? | Yes | [6 empty] | 0
2 | [8 empty] | 0
3 | Are hazardous materials stored appropriately? | n/a | [6 empty] | 0
Hazard identification - arson | [8 empty] | 0
4 | Are premises secure against arson by outsiders? | Yes |  | There is a secure entry system fitted to this building |  |  |  |  | 0
4 | [8 empty] | 0
5 | Are bins secured and stored in a suitable location? | Yes |  | The bins are secured (bin room) |  |  |  |  | 0
5 | [8 empty] | 0
6 | Is fire load close to the premises minimised? | Yes | [6 empty] | 0
6 | [8 empty] | 0
Hazard identification - smoking | [8 empty] | 0
7 | Smoking in inappropriate places. | No | [6 empty] | 0
7 | [8 empty] | 0
Hazard identification - any other issues - specify | [8 empty] | 0
8 | Is loft hatch secured | Yes |  | FB11 |  |  |  |  | 0
8 | [8 empty] | 0
Means of escape | [8 empty] | 0
9 | Is escape route design satisfactory? (see Home Office guides) | Yes |  | The escape stairs are satisfactory for the number of persons expected in the building at any given time |  |  |  |  | 0
9 | [8 empty] | 0
10 | Are escape routes clear and unobstructed? | Yes | [6 empty] | 0
10 | [8 empty] | 0
11 | Is number and provision of exits adequate? | Yes |  | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. |  |  |  |  | 0
11 | [8 empty] | 0
12 | Are doors on escape routes easily opened? | Yes | [6 empty] | 0
12 | [8 empty] | 0
13 | Are travel distances satisfactory - single and two-way? | Yes |  | The travel distances are satisfactory as per the recommendations in Approved Document B |  |  |  |  | 0
13 | [8 empty] | 0
14 | Are escape routes adequately protected? | No | P3 | All communal doors are in poor state of repair and should be repaired/replaced |  |  |  |  | 1
14 | Consider: storage and electrical cupboards, refuse chutes, fire doors (incl. provision, location, self-closers, strips and seals, | No | P3 | Cannot access above flat entrance doors due to false ceiling to confirm compartmentation |  |  |  |  | 2
14 | condition), stair ventilation | No | P1 | There is a hole in the ceiling of the electrical intake cupboard and this should be filled with a fire retardant foam filler so as to maintain the compartmentation. |  |  |  |  | 3
14 |  |  |  | Pram sheds secure |  |  |  |  | 3
14 |  | No | P3 | The electrical intake was checked, secure (FB1) and clear of storage. The intake door is FD30 standard and it is recommended that it is upgraded to FD30S standard in any future works improvement program. Last EIC 08/2010 |  |  |  |  | 4
14 |  | No | P3 | There is damage to FED's 8 and 35 and these doors should be replaced with FD30S doorsets in any future works improvement program |  |  |  |  | 5
14 |  | No | P3 | FED 17 is missing its fire rated letterbox and a new fire rated letterbox should be fitted to this FED |  |  |  |  | 6
14 |  |  |  | All FED's except for 8, 17 and 35 are FD30S standard doors |  |  |  |  | 6
14 | [8 empty] | 6
14 | [8 empty] | 6
15 | Are escape routes separated (where appropriate)? | Yes | [6 empty] | 6
15 | [8 empty] | 6
16 | Do escape routes lead to a place of safety? | Yes |  | All escape routes lead to open air at ground level. |  |  |  |  | 6
16 | [8 empty] | 6
17 | Are corridors sub-divided (where appropriate)? | Yes | [6 empty] | 6
17 | [8 empty] | 6
18 | Are floors free from slipping/tripping hazards? | No | P3 | Every stair nosing should be highlighted internally & externally with a minimum of a 25mm strip if photoluminescent or 50mm if plain white or yellow across the length of the front part of the step in order to achieve the required level of light reflectance (LRV 30 as a minimum). Existing stair nosings have been highlighted with a patterned stairnosing and are not to the required size which can be confusing for the visually impaired. These should be replaced with appropriate stair nosings in line with the guidance in ADM and BS8300. |  |  |  |  | 7
18 | [8 empty] | 7
19 | Is it considered that the building is provided with reasonable arrangements for means of escape of disabled people? | Yes | [6 empty] | 7
19 | [8 empty] | 7
Emergency escape lighting | [8 empty] | 7
20 | Is emergency escape lighting coverage sufficient (internal and external)? | No | P3 | Replace the light fittings within the staircase and entrance lobby with non-maintained emergency light fittings (NM3) at every change of level and direction (BS 5266 Part 1) as the existing fittings are not emergency light units. Alternatively, consideration should be given to fitting a Photoluminescent low level wayguidance system (PSPA Class D) in accordance with BS5266 part 6. |  |  |  |  | 8
20 | [8 empty] | 8
21 | Is emergency escape lighting in good working order? | n/a | [6 empty] | 8
21 | [8 empty] | 8
Signage | [8 empty] | 8
22 | Is there adequate provision of fire safety signs and notices? | No | P1 | Fit Danger Electricity and Fire Door Keep Locked Shut sign to intake cupboard door |  |  |  |  | 9
22 | [8 empty] | 9
22 | [8 empty] | 9
22 | [8 empty] | 9
22 | [8 empty] | 9
22 | [8 empty] | 9
23 | Are signs clearly visible and not obstructed? | Yes | [6 empty] | 9
23 | [8 empty] | 9
Fire detection and alarm | [8 empty] | 9
24 | Is automatic detection and/or manual alarm provided in the premises? If yes, describe system. | No | [6 empty] | 9
24 | [8 empty] | 9
25 | Is further automatic detection and/or manual alarm provision required? If yes, state what. | No | [6 empty] | 9
25 | [8 empty] | 9
26 | Is the fire alarm system in working order? | n/a | [6 empty] | 9
26 | [8 empty] | 9
Limiting fire spread | [8 empty] | 9
27 | Is the level of compartmentation adequate? (Special consideration should be given to converted or non 'purpose built' premises.) | Yes | [6 empty] | 9
27 | [8 empty] | 9
27 | [8 empty] | 9
27 | [8 empty] | 9
27 | [8 empty] | 9
28 | Are linings appropriate to limit fire spread? | Yes | [6 empty] | 9
28 | [8 empty] | 9
29 | Where required, are dampers provided? | n/a | [6 empty] | 9
29 | [8 empty] | 9
Fire fighting equipment | [8 empty] | 9
30 | Provision, accessibility and condition of portable fire extinguishers | n/a | [6 empty] | 9
30 | [8 empty] | 9
31 | Provision and condition of other fire extinguishing systems | n/a | [6 empty] | 9
31 | [8 empty] | 9
32 | Are dry/wet risers in good order? | Yes | [6 empty] | 9
32 | [8 empty] | 9
33 | Is fireman's switch working correctly? | Yes | [6 empty] | 9
33 | [8 empty] | 9
Other issues | [8 empty] | 9
34 | Roof void | Yes | [6 empty] | 9
35 | Internal stacks | Yes |  | internal |  |  |  |  | 9
36 | [8 empty] | 9
37 | [8 empty] | 9

## M-M
Priority | Description | Timescale |  |  |  |  | UPRN | B132A26
P0 | When an unacceptable risk to fire safety is present. Note - Works typically carried out by Housing/Repairs | Within 10 days | [7 empty] | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the RESPONSIVE REPAIRS TEAM | Within 6 months | [7 empty] | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year | [7 empty] | n/k | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years | [7 empty] | n/a | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years | [8 empty] | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural | [8 empty] | FRA Team
Premises: | Hudson 1-45, NW9 5YL ( |  |  | FRA undertaken on (date): | 2017-03-30
Question | Management/maintenance | Yes/No n/k-n/a | Priority | Location and comment | Ownership | Details | Ongoing from last FRA? | Completed date
Premises management | [8 empty] | 9
38 | Is there a suitable record of fire safety arrangements available? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  |  | 9
38 | [8 empty] | 9
39 | Are appropriate fire safety procedures in place? Consider: Emergency action plans; calling/meeting the fire service; ensuring the premises are evacuated; assembly points; assistance for disabled; information to external contractors; nominated staff duties | Yes |  | All responsibilities for fire safety have been addressed with Barnet Homes Fire Safety Policy. The policy is available to all staff on the company intranet. |  |  |  |  | 9
39 | [8 empty] | 9
40 | Has any liaison taken place with the local fire and rescue service? | Yes |  | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. |  |  |  |  | 9
40 | [8 empty] | 9
Training | [8 empty] | 9
41 | Do staff receive induction and/or annual fire safety refresher training? | Yes |  | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. |  |  |  |  | 9
41 | [8 empty] | 9
42 | If drills are considered appropriate, are they carried out at regular intervals? | n/a | [6 empty] | 9
42 | [8 empty] | 9
Maintenance checks | [8 empty] | 9
43 | Are the premises generally well maintained? | Yes |  | The building is generally well maintained with some minor defects that form part of the action plan |  |  |  |  | 9
43 | [8 empty] | 9
44 | Do appropriate regular checks take place? | Yes |  | Regular checks of the premises are carried out and any defects reported to the building maintenance office. |  |  |  |  | 9
44 | [8 empty] | 9
45 | Is the alarm system adequately maintained? | n/a | [6 empty] | 9
45 | [8 empty] | 9
46 | Is the escape lighting adequately maintained? | Yes |  | It appears to be adequately maintained (in the intake) |  |  |  |  | 9
46 | [8 empty] | 9
47 | Are fire extinguishers adequately maintained? | n/a | [6 empty] | 9
47 | [8 empty] | 9
48 | Are rising mains adequately maintained? | n/a | [6 empty] | 9
48 | [8 empty] | 9
49 | Are fireman lifts adequately maintained? | n/a | [6 empty] | 9
49 | [8 empty] | 9
50 | Is the sprinkler system adequately maintained? | n/a | [6 empty] | 9
50 | [8 empty] | 9
51 | Is the lightning protection system adequately maintained? | Yes |  | A schedule of maintenance is completed by Technical Services under a Service Level Agreement (SLA) |  |  |  |  | 9
51 | [8 empty] | 9
Records | [8 empty] | 9
52 | Are fire safety maintenance records available for the premises? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  |  | 9
52 | [8 empty] | 9
53 | Are fire drills recorded? | n/a | [6 empty] | 9
53 | [8 empty] | 9
54 | Is fire safety training recorded? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  |  | 9
54 | [8 empty] | 9
55 | Are fire alarm tests recorded? | n/a | [6 empty] | 9
55 | [8 empty] | 9
56 | Are emergency escape lighting tests recorded? | n/k |  | (and would only apply to the intake) |  |  |  |  | 9
56 | [8 empty] | 9
Other issues | [8 empty] | 9
57 | [8 empty] | 9
58 | [8 empty] | 9
59 | [8 empty] | 9
60 | [8 empty] | 9
61 | [8 empty] | 9
62 | [8 empty] | 9

## ActionPlan
| Priority | Description | Timescale |  |  | UPRN
| P0 | When an unacceptable risk to fire safety is present. Note - works typically carried out by Housing/Repairs | Within 10 days |  |  | B132A26 | No
| P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the RESPONSIVE REPAIRS TEAM | Within 6 months |  |  |  | n/a
| P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year
| P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years
| P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years
| P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural
Fire Risk Assessment - Action Plan
| Premises: | Hudson 1-45, NW9 5YL ( |  |  | FRA undertaken on (date): | 2017-03-30
| Question | Action to be taken | Priority | Ownership | Details | Ongoing from last FRA
1 | 14 | All communal doors are in poor state of repair and should be repaired/replaced | P3
2 | 14 | Cannot access above flat entrance doors due to false ceiling to confirm compartmentation | P3
3 | 14 | There is a hole in the ceiling of the electrical intake cupboard and this should be filled with a fire retardant foam filler so as to maintain the compartmentation. | P1
4 | 14 | The electrical intake was checked, secure (FB1) and clear of storage. The intake door is FD30 standard and it is recommended that it is upgraded to FD30S standard in any future works improvement program. Last EIC 08/2010 | P3
5 | 14 | There is damage to FED's 8 and 35 and these doors should be replaced with FD30S doorsets in any future works improvement program | P3
6 | 14 | FED 17 is missing its fire rated letterbox and a new fire rated letterbox should be fitted to this FED | P3
7 | 18 | Every stair nosing should be highlighted internally & externally with a minimum of a 25mm strip if photoluminescent or 50mm if plain white or yellow across the length of the front part of the step in order to achieve the required level of light reflectance (LRV 30 as a minimum). Existing stair nosings have been highlighted with a patterned stairnosing and are not to the required size which can be confusing for the visually impaired. These should be replaced with appropriate stair nosings in line with the guidance in ADM and BS8300. | P3
8 | 20 | Replace the light fittings within the staircase and entrance lobby with non-maintained emergency light fittings (NM3) at every change of level and direction (BS 5266 Part 1) as the existing fittings are not emergency light units. Alternatively, consideration should be given to fitting a Photoluminescent low level wayguidance system (PSPA Class D) in accordance with BS5266 part 6. | P3
9 | 22 | Fit Danger Electricity and Fire Door Keep Locked Shut sign to intake cupboard door | P1
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63

## Data (hidden)
KeyID | Question | Priority | Location and comment | Ownership | Details | Ongoing from last FRA
0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 2 | 0 | 0 | 0 | 0 | 0
0 | 2 | 0 | 0 | 0 | 0 | 0
0 | 3 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4 | 0 | There is a secure entry system fitted to this building | 0 | 0 | 0
0 | 4 | 0 | 0 | 0 | 0 | 0
0 | 5 | 0 | The bins are secured (bin room) | 0 | 0 | 0
0 | 5 | 0 | 0 | 0 | 0 | 0
0 | 6 | 0 | 0 | 0 | 0 | 0
0 | 6 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7 | 0 | 0 | 0 | 0 | 0
0 | 7 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8 | 0 | FB11 | 0 | 0 | 0
0 | 8 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 9 | 0 | The escape stairs are satisfactory for the number of persons expected in the building at any given time | 0 | 0 | 0
0 | 9 | 0 | 0 | 0 | 0 | 0
0 | 10 | 0 | 0 | 0 | 0 | 0
0 | 10 | 0 | 0 | 0 | 0 | 0
0 | 11 | 0 | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. | 0 | 0 | 0
0 | 11 | 0 | 0 | 0 | 0 | 0
0 | 12 | 0 | 0 | 0 | 0 | 0
0 | 12 | 0 | 0 | 0 | 0 | 0
0 | 13 | 0 | The travel distances are satisfactory as per the recommendations in Approved Document B | 0 | 0 | 0
0 | 13 | 0 | 0 | 0 | 0 | 0
1 | 14 | P3 | All communal doors are in poor state of repair and should be repaired/replaced | 0 | 0 | 0
2 | 14 | P3 | Cannot access above flat entrance doors due to false ceiling to confirm compartmentation | 0 | 0 | 0
3 | 14 | P1 | There is a hole in the ceiling of the electrical intake cupboard and this should be filled with a fire retardant foam filler so as to maintain the compartmentation. | 0 | 0 | 0
3 | 14 | 0 | Pram sheds secure | 0 | 0 | 0
4 | 14 | P3 | The electrical intake was checked, secure (FB1) and clear of storage. The intake door is FD30 standard and it is recommended that it is upgraded to FD30S standard in any future works improvement program. Last EIC 08/2010 | 0 | 0 | 0
5 | 14 | P3 | There is damage to FED's 8 and 35 and these doors should be replaced with FD30S doorsets in any future works improvement program | 0 | 0 | 0
6 | 14 | P3 | FED 17 is missing its fire rated letterbox and a new fire rated letterbox should be fitted to this FED | 0 | 0 | 0
6 | 14 | 0 | All FED's except for 8, 17 and 35 are FD30S standard doors | 0 | 0 | 0
6 | 14 | 0 | 0 | 0 | 0 | 0
6 | 14 | 0 | 0 | 0 | 0 | 0
6 | 15 | 0 | 0 | 0 | 0 | 0
6 | 15 | 0 | 0 | 0 | 0 | 0
6 | 16 | 0 | All escape routes lead to open air at ground level. | 0 | 0 | 0
6 | 16 | 0 | 0 | 0 | 0 | 0
6 | 17 | 0 | 0 | 0 | 0 | 0
6 | 17 | 0 | 0 | 0 | 0 | 0
7 | 18 | P3 | Every stair nosing should be highlighted internally & externally with a minimum of a 25mm strip if photoluminescent or 50mm if plain white or yellow across the length of the front part of the step in order to achieve the required level of light reflectance (LRV 30 as a minimum). Existing stair nosings have been highlighted with a patterned stairnosing and are not to the required size which can be confusing for the visually impaired. These should be replaced with appropriate stair nosings in line with the guidance in ADM and BS8300. | 0 | 0 | 0
7 | 18 | 0 | 0 | 0 | 0 | 0
7 | 19 | 0 | 0 | 0 | 0 | 0
7 | 19 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | P3 | Replace the light fittings within the staircase and entrance lobby with non-maintained emergency light fittings (NM3) at every change of level and direction (BS 5266 Part 1) as the existing fittings are not emergency light units. Alternatively, consideration should be given to fitting a Photoluminescent low level wayguidance system (PSPA Class D) in accordance with BS5266 part 6. | 0 | 0 | 0
8 | 20 | 0 | 0 | 0 | 0 | 0
8 | 21 | 0 | 0 | 0 | 0 | 0
8 | 21 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | P1 | Fit Danger Electricity and Fire Door Keep Locked Shut sign to intake cupboard door | 0 | 0 | 0
9 | 22 | 0 | 0 | 0 | 0 | 0
9 | 22 | 0 | 0 | 0 | 0 | 0
9 | 22 | 0 | 0 | 0 | 0 | 0
9 | 22 | 0 | 0 | 0 | 0 | 0
9 | 22 | 0 | 0 | 0 | 0 | 0
9 | 23 | 0 | 0 | 0 | 0 | 0
9 | 23 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 0 | 0 | 0 | 0 | 0
9 | 24 | 0 | 0 | 0 | 0 | 0
9 | 25 | 0 | 0 | 0 | 0 | 0
9 | 25 | 0 | 0 | 0 | 0 | 0
9 | 26 | 0 | 0 | 0 | 0 | 0
9 | 26 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 0 | 0 | 0 | 0 | 0
9 | 27 | 0 | 0 | 0 | 0 | 0
9 | 27 | 0 | 0 | 0 | 0 | 0
9 | 27 | 0 | 0 | 0 | 0 | 0
9 | 27 | 0 | 0 | 0 | 0 | 0
9 | 28 | 0 | 0 | 0 | 0 | 0
9 | 28 | 0 | 0 | 0 | 0 | 0
9 | 29 | 0 | 0 | 0 | 0 | 0
9 | 29 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 0 | 0 | 0 | 0 | 0
9 | 30 | 0 | 0 | 0 | 0 | 0
9 | 31 | 0 | 0 | 0 | 0 | 0
9 | 31 | 0 | 0 | 0 | 0 | 0
9 | 32 | 0 | 0 | 0 | 0 | 0
9 | 32 | 0 | 0 | 0 | 0 | 0
9 | 33 | 0 | 0 | 0 | 0 | 0
9 | 33 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0
9 | 34 | 0 | 0 | 0 | 0 | 0
9 | 35 | 0 | internal | 0 | 0 | 0
9 | 36 | 0 | 0 | 0 | 0 | 0
9 | 37 | 0 | 0 | 0 | 0 | 0
9 | 38 | 0 | Records are held centrally by the Health and Safety Team | 0 | 0 | 0
9 | 38 | 0 | 0 | 0 | 0 | 0
9 | 39 | 0 | All responsibilities for fire safety have been addressed with Barnet Homes Fire Safety Policy. The policy is available to all staff on the company intranet. | 0 | 0 | 0
9 | 39 | 0 | 0 | 0 | 0 | 0
9 | 40 | 0 | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. | 0 | 0 | 0
9 | 40 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0
9 | 41 | 0 | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. | 0 | 0 | 0
9 | 41 | 0 | 0 | 0 | 0 | 0
9 | 42 | 0 | 0 | 0 | 0 | 0
9 | 42 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0
9 | 43 | 0 | The building is generally well maintained with some minor defects that form part of the action plan | 0 | 0 | 0
9 | 43 | 0 | 0 | 0 | 0 | 0
9 | 44 | 0 | Regular checks of the premises are carried out and any defects reported to the building maintenance office. | 0 | 0 | 0
9 | 44 | 0 | 0 | 0 | 0 | 0
9 | 45 | 0 | 0 | 0 | 0 | 0
9 | 45 | 0 | 0 | 0 | 0 | 0
9 | 46 | 0 | It appears to be adequately maintained (in the intake) | 0 | 0 | 0
9 | 46 | 0 | 0 | 0 | 0 | 0
9 | 47 | 0 | 0 | 0 | 0 | 0
9 | 47 | 0 | 0 | 0 | 0 | 0
9 | 48 | 0 | 0 | 0 | 0 | 0
9 | 48 | 0 | 0 | 0 | 0 | 0
9 | 49 | 0 | 0 | 0 | 0 | 0
9 | 49 | 0 | 0 | 0 | 0 | 0
9 | 50 | 0 | 0 | 0 | 0 | 0
9 | 50 | 0 | 0 | 0 | 0 | 0
9 | 51 | 0 | A schedule of maintenance is completed by Technical Services under a Service Level Agreement (SLA) | 0 | 0 | 0
9 | 51 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0
9 | 52 | 0 | Records are held centrally by the Health and Safety Team | 0 | 0 | 0
9 | 52 | 0 | 0 | 0 | 0 | 0
9 | 53 | 0 | 0 | 0 | 0 | 0
9 | 53 | 0 | 0 | 0 | 0 | 0
9 | 54 | 0 | Records are held centrally by the Health and Safety Team | 0 | 0 | 0
9 | 54 | 0 | 0 | 0 | 0 | 0
9 | 55 | 0 | 0 | 0 | 0 | 0
9 | 55 | 0 | 0 | 0 | 0 | 0
9 | 56 | 0 | (and would only apply to the intake) | 0 | 0 | 0
9 | 56 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0
9 | 57 | 0 | 0 | 0 | 0 | 0
9 | 58 | 0 | 0 | 0 | 0 | 0
9 | 59 | 0 | 0 | 0 | 0 | 0
9 | 60 | 0 | 0 | 0 | 0 | 0
9 | 61 | 0 | 0 | 0 | 0 | 0
9 | 62 | 0 | 0 | 0 | 0 | 0