## FRA-detail
[6 empty] | UPRN | B95A1
Genereal needs flatted accommodation
Fire Risk Assessment (FRA)
Regulatory Reform (Fire Safety) Order 2005
184-188 | Next review due on *: |  | As FRA program
| Date of FRA: |  | 2017-06-30
| Responsible person (e.g. housing provider): |  |  | Chief Executive, Barnet Homes
| Fire Risk Assessor |  | The Fire Risk Assessment was undertaken by Mr Philip Holmes who has the necessary qualifications, competency and experience in Fire Risk Management that give him the status of “Competent Person” as described in articles 15 and 18 of the ‘Regulatory Reform (Fire Safety) Order 2005', for properties in England & Wales, and the 'Fire Safety (Scotland) Regulations 2006' for those in Scotland. This legislation now supersedes all previous fire legislation for England, Wales & Scotland and forms the ‘Fire Regulations'. He has been trained in all necessary disciplines of fire safety, building design and building behaviour under fire conditions and is considered to be sufficiently practised in the necessary skills to enable him to carry out a practical fire risk assessment.
(include relevant professional memberships and/or qualifications)
Address of premises: | Person managing fire safety for the premises: |  |  | Health & Safety Manager
Marsh Drive 73-96, NW9 7QE
| Did you consult with any other individual during the FRA? |  |  |  | No
| If yes, provide | Name
Position within company
| Recommended review date: |  | The person managing fire safety should monitor the progress of work undertaken in rectifying the deficiencies reported and should ensure that checks are undertaken at target completion dates. A follow up inspection (taking the form of an interim fire risk assessment review) should be undertaken no more than one month from the time when the reported ‘Priority P0’ deficiencies have been identified and additionally in six months by which time Priority P1 deficiencies should have been actioned. It is Barnet Homes policy that a review of the fire risk assessment will be undertaken no later than 12 months from the date of inspection.
Euro Compliance Limited
Company Registration: 06353434
Registered office: 90 Milton Avenue, Barnet, Herts, EN5 2EU
Members of the Institute of Fire Engineers
Yes
No

## Premises summary
[6 empty] | UPRN | B95A1
Premises: | Marsh Drive 73-96, NW9 7QE |  |  | FRA undertaken on (date): | 2017-06-30
Risk rating | Moderate | Risk rating legend | [5 empty] | Trivial
| The works listed in this report (Action Plan) are recommended to reduce the level of risk to (or maintain it at) Tolerable | [6 empty] | Tolerable
Moderate
Extent of common areas | [7 empty] | Substantial
Internal and external communal areas including the following: entrances, exits, escape stairs, landings, lobbies, electrical intake/service cupboards, pram shed areas, refuse areas. Ventilation - open balcony - 2 way MOE | [7 empty] | Intolerable
Details of building construction (approx. age, structure, cladding, walls, roof)
Concrete framed with brick walls and a pitched roof. |  | Low | Unusually low likelihood of fire as a result of negligible potential sources of ignition.
|  | Medium | Normal fire hazards (e.g. potential ignition sources) for this type of occupancy, with fire hazards generally subject to appropriate controls (other than minor shortcomings).
|  | High | Lack of adequate controls applied to one or more significant fire hazards, such as to result in significant increases in likelihood of fire.
|  | Slight harm | Outbreak of fire unlikely to result in serious injury or death of any occupant (other than an occupant sleeping in a room in which a fire occurs).
Details of building layout (number of flats, floors, staircases, lifts, etc.) |  | Moderate harm | Outbreak of fire could foreseeably result in injury (including serious injury) of one or more occupants, but it is unlikely to involve multiple fatalities.
24 flats, 6 floors, 2 staircases + ramps and shared lifts (not FF)
|  | Extreme harm | Significant potential for serious injury or death of one or more occupants.
|  | Risk level | Action and timescale
|  | Trivial | No action is required and no detailed records need be kept.
|  | Tolerable | No major additional controls required. However, there might be a need for improvements that involve minor or limited cost.
How are occupants who warrant special consideration identified? |  | Moderate | It is essential that efforts are made to reduce the risk. Risk reduction measures should be implemented within a defined time period. Where moderate risk is associated with consequences that constitute extreme harm, further assessment might be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures.
In the event of an emergency vulnerability is obtained from the OHMS database available to the Barnet Homes Emergency Officer
|  | Substantial | Considerable resources might have to be allocated to reduce the risk. If the building is unoccupied it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken.
Any other relevant information (including previous fire loss experience)
Barnet Homes Fire Policy and Procedure document forms part of the organisations' Health & Safety Policy and is reviewed by the Board on an annual basis.
|  | Intolerable | Building (or relevant areas) should not be occupied until the risk is reduced.
Areas where access was not available

## FRA
Priority | Description | Timescale |  |  | Over-All Block Risk Rating |  | UPRN | B95A1
P0 | When an unacceptable risk to fire safety is present. Note: Works typically carried out by Housing/Repairs | Within 10 days |  |  | Any |  |  |  | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the Note - RESPONSIVE REPAIRS TEAM | Within 6 months |  |  | Any |  |  |  | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year |  |  | Substantial |  |  |  | n/k | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years |  |  | Moderate |  |  |  | n/a | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years |  |  | Tolerable |  |  |  |  | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural |  |  | Ongoing |  |  |  |  | FRA Team
FIRE RISK ASSESSMENT
NOTE: Please note that whilst we state "recommendations" for the significant findings in this Fire Risk Assessment (Location and comment), these recommendations are the minimum requirements for the 'Responsible Person' in order to comply with the law, in this case the Regulatory Reform Fire Safety Order 2005. They are stated as our 'recommendations' because alternatives may be considered by the responsible person.
Premises: | Marsh Drive 73-96, NW9 7QE |  |  | FRA date: | 2017-06-30
Question | Fire safety measures | Yes/No n/k - n/a | Priority | Location and comment | Details | Ongoing from last FRA? | Completed date
Hazard identification - housekeeping | [7 empty] | 0
1 | Are combustibles separated from ignition sources? | Yes | [5 empty] | 0
1 | [7 empty] | 0
2 | Is unnecessary storage of combustible materials/waste avoided? | No | P0 | Remove bikes by flats 73, 75, 78 |  |  |  | 1
2 | [7 empty] | 1
3 | Are hazardous materials stored appropriately? | n/a | [5 empty] | 1
Hazard identification - arson | [7 empty] | 1
4 | Are premises secure against arson by outsiders? | No | P3 | There is no secure entry system fitted to this building and one should be considered in line with Barnet Homes policy |  |  |  | 2
4 | [7 empty] | 2
5 | Are bins secured and stored in a suitable location? | Yes | P3 | The bins are too close and should be secured away from the building |  |  |  | 3
5 | [7 empty] | 3
6 | Is fire load close to the premises minimised? | Yes |  | No evidence of fire loads near premises. |  |  |  | 3
6 | [7 empty] | 3
Hazard identification - smoking | [7 empty] | 3
7 | Smoking in inappropriate places. | No | [5 empty] | 3
7 | [7 empty] | 3
Hazard identification - any other issues - specify | [7 empty] | 3
8 | Is loft hatch secured | n/a | [5 empty] | 3
8 | [7 empty] | 3
Means of escape | [7 empty] | 3
9 | Is escape route design satisfactory? (see Home Office guides) | Yes |  | The escape route is satisfactory and meets the requirements of the Building Regulations ADB |  |  |  | 3
9 | [7 empty] | 3
10 | Are escape routes clear and unobstructed? | Yes | [5 empty] | 3
10 | [7 empty] | 3
11 | Is number and provision of exits adequate? | Yes |  | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. |  |  |  | 3
11 | [7 empty] | 3
12 | Are doors on escape routes easily opened? | n/a | [5 empty] | 3
12 | [7 empty] | 3
13 | Are travel distances satisfactory - single and two-way? | Yes |  | The travel distances are satisfactory and in line with the requirements of the Building Regulations, Approved Document B. Two directions of escape |  |  |  | 3
13 | [7 empty] | 3
14 | Are escape routes adequately protected? Consider: storage and electrical cupboards, refuse chutes, fire doors (incl. provision, location, self-closers, strips and seals, condition), stair ventilation | No | P3 | FD30 doors are not required as there are two directions of escape and flats are open balcony. However FD30S doors are required to flats 74-79 as these flats are to dead end condition. FED 74 is UPVC |  |  |  | 4
14 |  | Yes | P3 | Unable to access intake and risers (Gerda key). Last EIC 23/02/15 (from Jan 2017 FRA). Revisit required |  |  |  | 5
14 |  | Yes |  | The electrical intake door is an FD30S door |  |  |  | 5
14 |  | Yes |  | All pram shed doors are secured |  |  |  | 5
14 |  | No | P3 | Confirmation is required that all electrical ducting is fire rated and has relevant fire breaks, etc in place |  |  |  | 6
14 |  | No | P3 | FED's 75-79 are also on the single direction of escape and require fire rated and insulated glazing to a minimum height of 1.1m |  |  |  | 7
14 | [7 empty] | 7
14 | [7 empty] | 7
14 | [7 empty] | 7
14 | [7 empty] | 7
15 | Are escape routes separated (where appropriate)? | n/a | [5 empty] | 7
15 | [7 empty] | 7
16 | Do escape routes lead to a place of safety? | Yes |  | All escape routes lead to open air at ground level. |  |  |  | 7
16 | [7 empty] | 7
17 | Are corridors sub-divided (where appropriate)? | n/a | [5 empty] | 7
17 | [7 empty] | 7
18 | Are floors free from slipping/tripping hazards? | No | P3 | Every stair nosing needs to be highlighted internally & externally with a minimum of a 25mm strip across the full length of the front part of the step. Consideration should be given to fitting Photoluminescent nosings/strips in accordance to BS5266-6 as well or to HSE guidleines relating to slips, trips and falls particularly as staircases are the main means of escape for persons on the first floor or higher in any building. |  |  |  | 8
18 | [7 empty] | 8
19 | Is it considered that the building is provided with reasonable arrangements for means of escape of disabled people? | No |  | All stair nosings should be easily identifiable to visually impaired and blind persons as a matter of duty of care and should achieve the Light Reflectance Values as set out in ADM (a LRV of 30) particularly as these staircases are the main means of escape in the event of fire (for persons on the 1st floor). |  |  |  | 8
19 | [7 empty] | 8
Emergency escape lighting | [7 empty] | 8
20 | Is emergency escape lighting coverage sufficient (internal and external)? | No | P3 | There is emergency lighting fitted in this building but it has not been fitted to BS5266-1 and the light fittings have been fitted on the ceilings in the smoke reservoirs (Paragraph 6.4). It is therefore recommended that the emergency lighting is reconfigured to take into account paragraph 6.4 or alternatively that a low level emergency escape lighting system is fitted throughout the premises, including low level signage (Rule 43 recommendation). Consideration should be given to fitting a photoluminescent low level guidance system which should be fitted in accordance to the BS5266 series. |  |  |  | 9
20 | [7 empty] | 9
21 | Is emergency escape lighting in good working order? | n/k |  | Test date 27/07/16 |  |  |  | 9
21 | [7 empty] | 9
Signage | [7 empty] | 9
22 | Is there adequate provision of fire safety signs and notices? | No | P3 | Full fire safety signage survey recommended |  |  |  | 10
22 | [7 empty] | 10
22 | [7 empty] | 10
22 | [7 empty] | 10
22 | [7 empty] | 10
22 | [7 empty] | 10
23 | Are signs clearly visible and not obstructed? | Yes |  | Where fitted |  |  |  | 10
23 | [7 empty] | 10
Fire detection and alarm | [7 empty] | 10
24 | Is automatic detection and/or manual alarm provided in the premises? If yes, describe system. | n/k | P3 | It would be advisable to fit a BS5839-6 LD2 system to all flats if not already fitted. Review recommended. |  |  |  | 11
24 | [7 empty] | 11
25 | Is further automatic detection and/or manual alarm provision required? If yes, state what. | No | [5 empty] | 11
25 | [7 empty] | 11
26 | Is the fire alarm system in working order? | n/a | [5 empty] | 11
26 | [7 empty] | 11
Limiting fire spread | [7 empty] | 11
27 | Is the level of compartmentation adequate? (Special consideration should be given to converted or non 'purpose built' premises.) | n/k | P3 | The building has internal stacks. It is recommended that a sample survey of 2 or more flats is carried out to ensure that the compartmentation levels between flats is adequate as well as to the communal areas. |  |  |  | 12
27 | [7 empty] | 12
27 | [7 empty] | 12
27 | [7 empty] | 12
27 | [7 empty] | 12
28 | Are linings appropriate to limit fire spread? | No | P3 | There is paint delamination throughout the building and it should be removed and the area redecorated using Class 0 paint |  |  |  | 13
28 | [7 empty] | 13
29 | Where required, are dampers provided? | n/a | [5 empty] | 13
29 | [7 empty] | 13
Fire fighting equipment | [7 empty] | 13
30 | Provision, accessibility and condition of portable fire extinguishers | No |  | The communal areas should be sterile areas and as such it is considered that fire extinguishers are not required. It should be noted that fire extinguishers can pose a risk to life if used by untrained people. |  |  |  | 13
30 | [7 empty] | 13
31 | Provision and condition of other fire extinguishing systems | n/a | [5 empty] | 13
31 | [7 empty] | 13
32 | Are dry/wet risers in good order? | Yes |  | DRM appears to be in good working order (05/17) |  |  |  | 13
32 | [7 empty] | 13
33 | Is fireman's switch working correctly? | n/a | [5 empty] | 13
33 | [7 empty] | 13
Other issues | [7 empty] | 13
34 | Roof void? | Yes | [5 empty] | 13
35 | Other (specify) | [6 empty] | 13
36 | External cladding | Yes | P1 | The building has external cladding and it is recommended that a sample sheet is removed and tested to determine the level of combustibility of these panels |  |  |  | 14
37 | [7 empty] | 14

## M-M
Priority | Description | Timescale |  |  |  |  | UPRN | B95A1
P0 | When an unacceptable risk to fire safety is present. Note: Works typically carried out by Housing/Repairs | Within 10 days | [7 empty] | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the Note: RESPONSIVE REPAIRS TEAM | Within 6 months | [7 empty] | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note: PLANNED WORKS TEAM DELIVERY | Within 1 year | [7 empty] | n/k | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years | [7 empty] | n/a | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note: PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years | [8 empty] | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural | [8 empty] | FRA Team
Management and maintenance
Premises: | Marsh Drive 73-96, NW9 7QE |  |  | FRA date: | 2017-06-30
Question | Management/maintenance | Yes/No n/k - n/a | Priority | Location and comment | Details | Ongoing from last FRA? | Completed date
Premises management | [7 empty] | 14
38 | Is there a suitable record of fire safety arrangements available? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  | 14
38 | [7 empty] | 14
39 | Are appropriate fire safety procedures in place? Consider: Emergency action plans; calling/meeting the fire service; ensuring the premises are evacuated; assembly points; assistance for disabled; information to external contractors; nominated staff duties | Yes |  | All responsibilities for fire safety have been addressed with Barnet Homes Fire Safety Policy. The policy is available to all staff on the company intranet. |  |  |  | 14
39 | [7 empty] | 14
40 | Has any liaison taken place with the local fire and rescue service? | Yes |  | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. |  |  |  | 14
40 | [7 empty] | 14
Training | [7 empty] | 14
41 | Do staff receive induction and/or annual fire safety refresher training? | Yes |  | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. |  |  |  | 14
41 | [7 empty] | 14
42 | If drills are considered appropriate, are they carried out at regular intervals? | n/a | [5 empty] | 14
42 | [7 empty] | 14
Maintenance checks | [7 empty] | 14
43 | Are the premises generally well maintained? | Yes |  | The building is generally well maintained with some minor defects that form part of the action plan |  |  |  | 14
43 | [7 empty] | 14
44 | Do appropriate regular checks take place? | Yes |  | Regular checks of the premises are carried out and any defects reported to the building maintenance office. |  |  |  | 14
44 | [7 empty] | 14
45 | Is the alarm system adequately maintained? | n/a | [5 empty] | 14
45 | [7 empty] | 14
46 | Is the escape lighting adequately maintained? | n/k | P4 | Check emergency lighting records |  |  |  | 15
46 | [7 empty] | 15
47 | Are fire extinguishers adequately maintained? | n/a | [5 empty] | 15
47 | [7 empty] | 15
48 | Are rising mains adequately maintained? | n/k | P4 | Check DRM records |  |  |  | 16
48 | [7 empty] | 16
49 | Are fireman lifts adequately maintained? | n/a | [5 empty] | 16
49 | [7 empty] | 16
50 | Is the sprinkler system adequately maintained? | n/a | [5 empty] | 16
50 | [7 empty] | 16
51 | Is the lightning protection system adequately maintained? | Yes |  | A schedule of maintenance is completed by Technical Services under a Service Level Agreement (SLA) |  |  |  | 16
51 | [7 empty] | 16
Records | [7 empty] | 16
52 | Are fire safety maintenance records available for the premises? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  | 16
52 | [7 empty] | 16
53 | Are fire drills recorded? | n/a | [5 empty] | 16
53 | [7 empty] | 16
54 | Is fire safety training recorded? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  | 16
54 | [7 empty] | 16
55 | Are fire alarm tests recorded? | n/a | [5 empty] | 16
55 | [7 empty] | 16
56 | Are emergency escape lighting tests recorded? | n/k |  | It is understood that emergency lighting test records are kept centrally by Barnet Homes |  |  |  | 16
56 | [7 empty] | 16
Other issues | [8 empty] | 16
57 | [7 empty] | 16
58 | [7 empty] | 16
59 | [7 empty] | 16
60 | [7 empty] | 16
61 | [7 empty] | 16
62 | [7 empty] | 16

## ActionPlan
| Priority | Description | Timescale |  |  | UPRN |  | No
| P0 | When an unacceptable risk to fire safety is present. Works typically carried out by Housing/Repairs) | Within 10 days |  |  | B95A1 |  | n/a
| P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the RESPONSIVE REPAIRS TEAM | Within 6 months
| P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year
| P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years
| P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years.
| P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural
FIRE RISK ASSESSMENT ACTION PLAN
| Premises: | Marsh Drive 73-96, NW9 7QE |  |  |  | FRA date: | 2017-06-30
| Question | Action to be taken | Priority | Details | Ongoing from last FRA
1 | 2 | Remove bikes by flats 73, 75, 78 | P0
2 | 4 | There is no secure entry system fitted to this building and one should be considered in line with Barnet Homes policy | P3
3 | 5 | The bins are too close and should be secured away from the building | P3
4 | 14 | FD30 doors are not required as there are two directions of escape and flats are open balcony. However FD30S doors are required to flats 74-79 as these flats are to dead end condition. FED 74 is UPVC | P3
5 | 14 | Unable to access intake and risers (Gerda key). Last EIC 23/02/15 (from Jan 2017 FRA). Revisit required | P3
6 | 14 | Confirmation is required that all electrical ducting is fire rated and has relevant fire breaks, etc in place | P3
7 | 14 | FED's 75-79 are also on the single direction of escape and require fire rated and insulated glazing to a minimum height of 1.1m | P3
8 | 18 | Every stair nosing needs to be highlighted internally & externally with a minimum of a 25mm strip across the full length of the front part of the step. Consideration should be given to fitting Photoluminescent nosings/strips in accordance to BS5266-6 as well or to HSE guidleines relating to slips, trips and falls particularly as staircases are the main means of escape for persons on the first floor or higher in any building. | P3
9 | 20 | There is emergency lighting fitted in this building but it has not been fitted to BS5266-1 and the light fittings have been fitted on the ceilings in the smoke reservoirs (Paragraph 6.4). It is therefore recommended that the emergency lighting is reconfigured to take into account paragraph 6.4 or alternatively that a low level emergency escape lighting system is fitted throughout the premises, including low level signage (Rule 43 recommendation). Consideration should be given to fitting a photoluminescent low level guidance system which should be fitted in accordance to the BS5266 series. | P3
10 | 22 | Full fire safety signage survey recommended | P3
11 | 24 | It would be advisable to fit a BS5839-6 LD2 system to all flats if not already fitted. Review recommended. | P3
12 | 27 | The building has internal stacks. It is recommended that a sample survey of 2 or more flats is carried out to ensure that the compartmentation levels between flats is adequate as well as to the communal areas. | P3
13 | 28 | There is paint delamination throughout the building and it should be removed and the area redecorated using Class 0 paint | P3
14 | 36 | The building has external cladding and it is recommended that a sample sheet is removed and tested to determine the level of combustibility of these panels | P1
15 | 46 | Check emergency lighting records | P4
16 | 48 | Check DRM records | P4
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63

## Data (hidden)
KeyID | Question | Priority | Location and comment | Ownership | Details | Ongoing from last FRA
0 | 1 | 0 | 0 | #REF! | 0 | 0
0 | 1 | 0 | 0 | #REF! | 0 | 0
1 | 2 | P0 | Remove bikes by flats 73, 75, 78 | #REF! | 0 | 0
1 | 2 | 0 | 0 | #REF! | 0 | 0
1 | 3 | 0 | 0 | #REF! | 0 | 0
1 | 0 | 0 | 0 | #REF! | 0 | 0
2 | 4 | P3 | There is no secure entry system fitted to this building and one should be considered in line with Barnet Homes policy | #REF! | 0 | 0
2 | 4 | 0 | 0 | #REF! | 0 | 0
3 | 5 | P3 | The bins are too close and should be secured away from the building | #REF! | 0 | 0
3 | 5 | 0 | 0 | #REF! | 0 | 0
3 | 6 | 0 | No evidence of fire loads near premises. | #REF! | 0 | 0
3 | 6 | 0 | 0 | #REF! | 0 | 0
3 | 0 | 0 | 0 | #REF! | 0 | 0
3 | 7 | 0 | 0 | #REF! | 0 | 0
3 | 7 | 0 | 0 | #REF! | 0 | 0
3 | 0 | 0 | 0 | #REF! | 0 | 0
3 | 8 | 0 | 0 | #REF! | 0 | 0
3 | 8 | 0 | 0 | #REF! | 0 | 0
3 | 0 | 0 | 0 | #REF! | 0 | 0
3 | 9 | 0 | The escape route is satisfactory and meets the requirements of the Building Regulations ADB | #REF! | 0 | 0
3 | 9 | 0 | 0 | #REF! | 0 | 0
3 | 10 | 0 | 0 | #REF! | 0 | 0
3 | 10 | 0 | 0 | #REF! | 0 | 0
3 | 11 | 0 | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. | #REF! | 0 | 0
3 | 11 | 0 | 0 | #REF! | 0 | 0
3 | 12 | 0 | 0 | #REF! | 0 | 0
3 | 12 | 0 | 0 | #REF! | 0 | 0
3 | 13 | 0 | The travel distances are satisfactory and in line with the requirements of the Building Regulations, Approved Document B. Two directions of escape | #REF! | 0 | 0
3 | 13 | 0 | 0 | #REF! | 0 | 0
4 | 14 | P3 | FD30 doors are not required as there are two directions of escape and flats are open balcony. However FD30S doors are required to flats 74-79 as these flats are to dead end condition. FED 74 is UPVC | #REF! | 0 | 0
5 | 14 | P3 | Unable to access intake and risers (Gerda key). Last EIC 23/02/15 (from Jan 2017 FRA). Revisit required | #REF! | 0 | 0
5 | 14 | 0 | The electrical intake door is an FD30S door | #REF! | 0 | 0
5 | 14 | 0 | All pram shed doors are secured | #REF! | 0 | 0
6 | 14 | P3 | Confirmation is required that all electrical ducting is fire rated and has relevant fire breaks, etc in place | #REF! | 0 | 0
7 | 14 | P3 | FED's 75-79 are also on the single direction of escape and require fire rated and insulated glazing to a minimum height of 1.1m | #REF! | 0 | 0
7 | 14 | 0 | 0 | #REF! | 0 | 0
7 | 14 | 0 | 0 | #REF! | 0 | 0
7 | 14 | 0 | 0 | #REF! | 0 | 0
7 | 14 | 0 | 0 | #REF! | 0 | 0
7 | 15 | 0 | 0 | #REF! | 0 | 0
7 | 15 | 0 | 0 | #REF! | 0 | 0
7 | 16 | 0 | All escape routes lead to open air at ground level. | #REF! | 0 | 0
7 | 16 | 0 | 0 | #REF! | 0 | 0
7 | 17 | 0 | 0 | #REF! | 0 | 0
7 | 17 | 0 | 0 | #REF! | 0 | 0
8 | 18 | P3 | Every stair nosing needs to be highlighted internally & externally with a minimum of a 25mm strip across the full length of the front part of the step. Consideration should be given to fitting Photoluminescent nosings/strips in accordance to BS5266-6 as well or to HSE guidleines relating to slips, trips and falls particularly as staircases are the main means of escape for persons on the first floor or higher in any building. | #REF! | 0 | 0
8 | 18 | 0 | 0 | #REF! | 0 | 0
8 | 19 | 0 | All stair nosings should be easily identifiable to visually impaired and blind persons as a matter of duty of care and should achieve the Light Reflectance Values as set out in ADM (a LRV of 30) particularly as these staircases are the main means of escape in the event of fire (for persons on the 1st floor). | #REF! | 0 | 0
8 | 19 | 0 | 0 | #REF! | 0 | 0
8 | 0 | 0 | 0 | #REF! | 0 | 0
9 | 20 | P3 | There is emergency lighting fitted in this building but it has not been fitted to BS5266-1 and the light fittings have been fitted on the ceilings in the smoke reservoirs (Paragraph 6.4). It is therefore recommended that the emergency lighting is reconfigured to take into account paragraph 6.4 or alternatively that a low level emergency escape lighting system is fitted throughout the premises, including low level signage (Rule 43 recommendation). Consideration should be given to fitting a photoluminescent low level guidance system which should be fitted in accordance to the BS5266 series. | #REF! | 0 | 0
9 | 20 | 0 | 0 | #REF! | 0 | 0
9 | 21 | 0 | Test date 27/07/16 | #REF! | 0 | 0
9 | 21 | 0 | 0 | #REF! | 0 | 0
9 | 0 | 0 | 0 | #REF! | 0 | 0
10 | 22 | P3 | Full fire safety signage survey recommended | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 23 | 0 | Where fitted | #REF! | 0 | 0
10 | 23 | 0 | 0 | #REF! | 0 | 0
10 | 0 | 0 | 0 | #REF! | 0 | 0
11 | 24 | P3 | It would be advisable to fit a BS5839-6 LD2 system to all flats if not already fitted. Review recommended. | #REF! | 0 | 0
11 | 24 | 0 | 0 | #REF! | 0 | 0
11 | 25 | 0 | 0 | #REF! | 0 | 0
11 | 25 | 0 | 0 | #REF! | 0 | 0
11 | 26 | 0 | 0 | #REF! | 0 | 0
11 | 26 | 0 | 0 | #REF! | 0 | 0
11 | 0 | 0 | 0 | #REF! | 0 | 0
12 | 27 | P3 | The building has internal stacks. It is recommended that a sample survey of 2 or more flats is carried out to ensure that the compartmentation levels between flats is adequate as well as to the communal areas. | #REF! | 0 | 0
12 | 27 | 0 | 0 | #REF! | 0 | 0
12 | 27 | 0 | 0 | #REF! | 0 | 0
12 | 27 | 0 | 0 | #REF! | 0 | 0
12 | 27 | 0 | 0 | #REF! | 0 | 0
13 | 28 | P3 | There is paint delamination throughout the building and it should be removed and the area redecorated using Class 0 paint | #REF! | 0 | 0
13 | 28 | 0 | 0 | #REF! | 0 | 0
13 | 29 | 0 | 0 | #REF! | 0 | 0
13 | 29 | 0 | 0 | #REF! | 0 | 0
13 | 0 | 0 | 0 | #REF! | 0 | 0
13 | 30 | 0 | The communal areas should be sterile areas and as such it is considered that fire extinguishers are not required. It should be noted that fire extinguishers can pose a risk to life if used by untrained people. | #REF! | 0 | 0
13 | 30 | 0 | 0 | #REF! | 0 | 0
13 | 31 | 0 | 0 | #REF! | 0 | 0
13 | 31 | 0 | 0 | #REF! | 0 | 0
13 | 32 | 0 | DRM appears to be in good working order (05/17) | #REF! | 0 | 0
13 | 32 | 0 | 0 | #REF! | 0 | 0
13 | 33 | 0 | 0 | #REF! | 0 | 0
13 | 33 | 0 | 0 | #REF! | 0 | 0
13 | 0 | 0 | 0 | #REF! | 0 | 0
13 | 34 | 0 | 0 | #REF! | 0 | 0
13 | 35 | 0 | 0 | #REF! | 0 | 0
14 | 36 | P1 | The building has external cladding and it is recommended that a sample sheet is removed and tested to determine the level of combustibility of these panels | #REF! | 0 | 0
14 | 37 | 0 | 0 | #REF! | 0 | 0
14 | 38 | 0 | Records are held centrally by the Health and Safety Team | #REF! | 0 | 0
14 | 38 | 0 | 0 | #REF! | 0 | 0
14 | 39 | 0 | All responsibilities for fire safety have been addressed with Barnet Homes Fire Safety Policy. The policy is available to all staff on the company intranet. | #REF! | 0 | 0
14 | 39 | 0 | 0 | #REF! | 0 | 0
14 | 40 | 0 | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. | #REF! | 0 | 0
14 | 40 | 0 | 0 | #REF! | 0 | 0
14 | 0 | 0 | 0 | #REF! | 0 | 0
14 | 41 | 0 | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. | #REF! | 0 | 0
14 | 41 | 0 | 0 | #REF! | 0 | 0
14 | 42 | 0 | 0 | #REF! | 0 | 0
14 | 42 | 0 | 0 | #REF! | 0 | 0
14 | 0 | 0 | 0 | #REF! | 0 | 0
14 | 43 | 0 | The building is generally well maintained with some minor defects that form part of the action plan | #REF! | 0 | 0
14 | 43 | 0 | 0 | #REF! | 0 | 0
14 | 44 | 0 | Regular checks of the premises are carried out and any defects reported to the building maintenance office. | #REF! | 0 | 0
14 | 44 | 0 | 0 | #REF! | 0 | 0
14 | 45 | 0 | 0 | #REF! | 0 | 0
14 | 45 | 0 | 0 | #REF! | 0 | 0
15 | 46 | P4 | Check emergency lighting records | #REF! | 0 | 0
15 | 46 | 0 | 0 | #REF! | 0 | 0
15 | 47 | 0 | 0 | #REF! | 0 | 0
15 | 47 | 0 | 0 | #REF! | 0 | 0
16 | 48 | P4 | Check DRM records | #REF! | 0 | 0
16 | 48 | 0 | 0 | #REF! | 0 | 0
16 | 49 | 0 | 0 | #REF! | 0 | 0
16 | 49 | 0 | 0 | #REF! | 0 | 0
16 | 50 | 0 | 0 | #REF! | 0 | 0
16 | 50 | 0 | 0 | #REF! | 0 | 0
16 | 51 | 0 | A schedule of maintenance is completed by Technical Services under a Service Level Agreement (SLA) | #REF! | 0 | 0
16 | 51 | 0 | 0 | #REF! | 0 | 0
16 | 0 | 0 | 0 | #REF! | 0 | 0
16 | 52 | 0 | Records are held centrally by the Health and Safety Team | #REF! | 0 | 0
16 | 52 | 0 | 0 | #REF! | 0 | 0
16 | 53 | 0 | 0 | #REF! | 0 | 0
16 | 53 | 0 | 0 | #REF! | 0 | 0
16 | 54 | 0 | Records are held centrally by the Health and Safety Team | #REF! | 0 | 0
16 | 54 | 0 | 0 | #REF! | 0 | 0
16 | 55 | 0 | 0 | #REF! | 0 | 0
16 | 55 | 0 | 0 | #REF! | 0 | 0
16 | 56 | 0 | It is understood that emergency lighting test records are kept centrally by Barnet Homes | #REF! | 0 | 0
16 | 56 | 0 | 0 | #REF! | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0
16 | 57 | 0 | 0 | #REF! | 0 | 0
16 | 58 | 0 | 0 | #REF! | 0 | 0
16 | 59 | 0 | 0 | #REF! | 0 | 0
16 | 60 | 0 | 0 | #REF! | 0 | 0
16 | 61 | 0 | 0 | #REF! | 0 | 0
16 | 62 | 0 | 0 | #REF! | 0 | 0