## FRA-detail
[6 empty] | UPRN | G647
General needs flatted accommodation
Fire Risk Assessment (FRA)
Regulatory Reform (Fire Safety) Order 2005
585-88 | Next review due on *: |  | As FRA program
| Date of FRA: |  | 2017-02-10
| Responsible person (e.g. housing provider): |  |  | Chief Executive, Barnet Homes
| Fire Risk Assessor |  | The Fire Risk Assessment was undertaken by Mr Haddon McLean who has the necessary qualifications, competency and experience in Fire Risk Management that give him the status of “Competent Person” as described in articles 15 and 18 of the ‘Regulatory Reform (Fire Safety) Order 2005', for properties in England & Wales, and the 'Fire Safety (Scotland) Regulations 2006' for those in Scotland. This legislation now supersedes all previous fire legislation for England, Wales & Scotland and forms the ‘Fire Regulations'. He has been trained in all necessary disciplines of fire safety, building design and building behaviour under fire conditions and is considered to be sufficiently practised in the necessary skills to enable him to carry out a practical fire risk assessment.
(include relevant professional memberships and/or qualifications)
Address of premises: | Person managing fire safety for the premises: |  |  | Health & Safety Manager
Tadbourne Court 1-4, HA8 9D
| Did you consult with any other individual during the FRA? |  |  |  | No
| If yes, provide | Name
Position within company
| Recommended review date: |  | The person managing fire safety should monitor the progress of work undertaken in rectifying the deficiencies reported and should ensure that checks are undertaken at target completion dates. A follow up inspection (taking the form of an interim fire risk assessment review) should be undertaken no more than one month from the time when the reported ‘Priority P0’ deficiencies have been identified and additionally in six months by which time Priority P1 deficiencies should have been actioned. It is Barnet Homes policy that a review of the fire risk assessment will be undertaken no later than 12 months from the date of inspection.
Euro Compliance Limited
Company Registration: 06353434
Registered office: 90 Milton Avenue, Barnet, Herts, EN5 2EU
Members of the Institute of Fire Engineers
Yes
No

## Premises summary
[6 empty] | UPRN | G647
Premises: | Tadbourne Court 1-4, HA8 9D |  |  | FRA undertaken on (date): | 2017-02-10
Risk rating | Moderate | Risk rating legend | [5 empty] | Trivial
| The works listed in this report (Action Plan) are recommended to reduce the level of risk to (or maintain it at) Tolerable | [6 empty] | Tolerable
Moderate
Extent of common areas | [7 empty] | Substantial
Internal and external communal areas including the following: entrances, exits, escape stairs, landings, lobbies, electrical intake/service cupboards, pram shed areas, refuse areas. Ventilation - openable windows | [7 empty] | Intolerable
Details of building construction (approx. age, structure, cladding, walls, roof)
Concrete framed with brick walls and a pitched roof. |  | Low | Unusually low likelihood of fire as a result of negligible potential sources of ignition.
|  | Medium | Normal fire hazards (e.g. potential ignition sources) for this type of occupancy, with fire hazards generally subject to appropriate controls (other than minor shortcomings).
|  | High | Lack of adequate controls applied to one or more significant fire hazards, such as to result in significant increases in likelihood of fire.
|  | Slight harm | Outbreak of fire unlikely to result in serious injury or death of any occupant (other than an occupant sleeping in a room in which a fire occurs).
Details of building layout (number of flats, floors, staircases, lifts, etc.) |  | Moderate harm | Outbreak of fire could foreseeably result in injury (including serious injury) of one or more occupants, but it is unlikely to involve multiple fatalities.
4 flats, 2 floors, 1 staircase and 0 lift
|  | Extreme harm | Significant potential for serious injury or death of one or more occupants.
|  | Risk level | Action and timescale
|  | Trivial | No action is required and no detailed records need be kept.
|  | Tolerable | No major additional controls required. However, there might be a need for improvements that involve minor or limited cost.
How are occupants who warrant special consideration identified? |  | Moderate | It is essential that efforts are made to reduce the risk. Risk reduction measures should be implemented within a defined time period. Where moderate risk is associated with consequences that constitute extreme harm, further assessment might be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures.
In the event of an emergency vulnerability is obtained from the OHMS database available to the Barnet Homes Emergency Officer
|  | Substantial | Considerable resources might have to be allocated to reduce the risk. If the building is unoccupied it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken.
Any other relevant information (including previous fire loss experience)
Barnet Homes Fire Policy and Procedure document forms part of the organisations' Health & Safety Policy and is reviewed by the Board on an annual basis.
|  | Intolerable | Building (or relevant areas) should not be occupied until the risk is reduced.
Areas where access was not available

## FRA
Priority | Description | Timescale |  |  | Over-All Block Risk Rating |  | UPRN | G647
P0 | When an unacceptable risk to fire safety is present. Note: Works typically carried out by Housing/Repairs | Within 10 days |  |  | Any |  |  |  | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the Note - RESPONSIVE REPAIRS TEAM | Within 6 months |  |  | Any |  |  |  | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year |  |  | Substantial |  |  |  | n/k | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years |  |  | Moderate |  |  |  | n/a | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years |  |  | Tolerable |  |  |  |  | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural |  |  | Ongoing |  |  |  |  | FRA Team
FIRE RISK ASSESSMENT
NOTE: Please note that whilst we state "recommendations" for the significant findings in this Fire Risk Assessment (Location and comment), these recommendations are the minimum requirements for the 'Responsible Person' in order to comply with the law, in this case the Regulatory Reform Fire Safety Order 2005. They are stated as our 'recommendations' because alternatives may be considered by the responsible person.
Premises: | Tadbourne Court 1-4, HA8 9D |  |  | FRA date: | 2017-02-10
Question | Fire safety measures | Yes/No n/k - n/a | Priority | Location and comment | Details | Ongoing from last FRA? | Completed date
Hazard identification - housekeeping | [7 empty] | 0
1 | Are combustibles separated from ignition sources? | Yes | [5 empty] | 0
1 | [7 empty] | 0
2 | Is unnecessary storage of combustible materials/waste avoided? | Yes | [5 empty] | 0
2 | [7 empty] | 0
3 | Are hazardous materials stored appropriately? | n/a | [5 empty] | 0
Hazard identification - arson | [7 empty] | 0
4 | Are premises secure against arson by outsiders? | Yes |  | There is a secure entry system fitted to this building |  |  |  | 0
4 | [7 empty] | 0
5 | Are bins secured and stored in a suitable location? | Yes |  | The bins are located in a satisfactory position. |  |  |  | 0
5 | [7 empty] | 0
6 | Is fire load close to the premises minimised? | Yes |  | No evidence of fire loads near premises. |  |  |  | 0
6 | [7 empty] | 0
Hazard identification - smoking | [7 empty] | 0
7 | Smoking in inappropriate places. | No | [5 empty] | 0
7 | [7 empty] | 0
Hazard identification - any other issues - specify | [7 empty] | 0
8 | Is loft hatch secured | n/a | [5 empty] | 0
8 | [7 empty] | 0
Means of escape | [7 empty] | 0
9 | Is escape route design satisfactory? (see Home Office guides) | Yes |  | The escape route is satisfactory and meets the requirements of the Building Regulations ADB |  |  |  | 0
9 | [7 empty] | 0
10 | Are escape routes clear and unobstructed? | Yes | [5 empty] | 0
10 | [7 empty] | 0
11 | Is number and provision of exits adequate? | Yes |  | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. |  |  |  | 0
11 | [7 empty] | 0
12 | Are doors on escape routes easily opened? | n/a | [5 empty] | 0
12 | [7 empty] | 0
13 | Are travel distances satisfactory - single and two-way? | Yes |  | The travel distances are satisfactory and in line with the requirements of the Building Regulations, Approved Document B. |  |  |  | 0
13 | [7 empty] | 0
14 | Are escape routes adequately protected? Consider: storage and electrical cupboards, refuse chutes, fire doors (incl. provision, location, self-closers, strips and seals, condition), stair ventilation | No | P3 | All flat entrance doors (FEDs) in this building are FD30S doors except FED 4 (pic 587) and this door should should be replaced with a certified FD30S door/doorset which should be fitted in accordance to BS8214. |  |  |  | 1
14 |  | Yes |  | Electrical intake not located in the common parts |  |  |  | 1
14 | [7 empty] | 1
14 |  | No | P3 | All pram shed doors are secure, QA check required to confirm fire rating. No significant risk. |  |  |  | 2
14 | [7 empty] | 2
14 | [7 empty] | 2
14 | [7 empty] | 2
14 | [7 empty] | 2
14 | [7 empty] | 2
14 | [7 empty] | 2
15 | Are escape routes separated (where appropriate)? | n/a | [5 empty] | 2
15 | [7 empty] | 2
16 | Do escape routes lead to a place of safety? | Yes |  | All escape routes lead to open air at ground level. |  |  |  | 2
16 | [7 empty] | 2
17 | Are corridors sub-divided (where appropriate)? | n/a | [5 empty] | 2
17 | [7 empty] | 2
18 | Are floors free from slipping/tripping hazards? | Yes |  | Every stair nosing needs to be highlighted internally & externally with a minimum of a 25mm strip across the full length of the front part of the step. Consideration should be given to fitting Photoluminescent nosings/strips in accordance to BS5266-6 as well or to HSE guidleines relating to slips, trips and falls particularly as staircases are the main means of escape for persons on the first floor or higher in any building. Existing nosings are highlighted with appropriate photoluminescent nosings |  |  |  | 2
18 | [7 empty] | 2
19 | Is it considered that the building is provided with reasonable arrangements for means of escape of disabled people? | Yes |  | All stair nosings should be easily identifiable to visually impaired and blind persons as a matter of duty of care and should achieve the Light Reflectance Values as set out in ADM (a LRV of 30) particularly as these staircases are the main means of escape in the event of fire (for persons on the 1st floor). |  |  |  | 2
19 | [7 empty] | 2
Emergency escape lighting | [7 empty] | 2
20 | Is emergency escape lighting coverage sufficient (internal and external)? | n/a |  | There is emergency lighting fitted in this building, it has not been fitted to standard but it is not required |  |  |  | 2
20 | [7 empty] | 2
21 | Is emergency escape lighting in good working order? | n/k | [5 empty] | 2
21 | [7 empty] | 2
Signage | [7 empty] | 2
22 | Is there adequate provision of fire safety signs and notices? | Yes | [5 empty] | 2
22 | [7 empty] | 2
22 | [7 empty] | 2
22 | [7 empty] | 2
22 | [7 empty] | 2
22 | [7 empty] | 2
23 | Are signs clearly visible and not obstructed? | n/a | [5 empty] | 2
23 | [7 empty] | 2
Fire detection and alarm | [7 empty] | 2
24 | Is automatic detection and/or manual alarm provided in the premises? If yes, describe system. | Yes | P3 | There are call points and sounders in the common areas but no fire alarm panel. A fire alarm system in the common parts of this building is not required and we would recommend a review of the fire strategy for this building, evac plan, etc and if necessary this part of the fire alarm system should be removed. It would be advisable to fit a BS5839-6 LD2 system to all flats if not already fitted. Review recommended. |  |  |  | 3
24 | [7 empty] | 3
25 | Is further automatic detection and/or manual alarm provision required? If yes, state what. | No | [5 empty] | 3
25 | [7 empty] | 3
26 | Is the fire alarm system in working order? | n/k | [5 empty] | 3
26 | [7 empty] | 3
Limiting fire spread | [7 empty] | 3
27 | Is the level of compartmentation adequate? (Special consideration should be given to converted or non 'purpose built' premises.) | n/k | P3 | It is not known if the building has internal or external stacks. It is recommended that an internal flat survey is carried out to ensure that the compartmentation levels between flats is adequate. |  |  |  | 4
27 | [7 empty] | 4
27 | [7 empty] | 4
27 | [7 empty] | 4
27 | [7 empty] | 4
28 | Are linings appropriate to limit fire spread? | Yes | [5 empty] | 4
28 | [7 empty] | 4
29 | Where required, are dampers provided? | n/a | [5 empty] | 4
29 | [7 empty] | 4
Fire fighting equipment | [7 empty] | 4
30 | Provision, accessibility and condition of portable fire extinguishers | No |  | The communal areas should be sterile areas and as such it is considered that fire extinguishers are not required. It should be noted that fire extinguishers can pose a risk to life if used by untrained people. |  |  |  | 4
30 | [7 empty] | 4
31 | Provision and condition of other fire extinguishing systems | n/a | [5 empty] | 4
31 | [7 empty] | 4
32 | Are dry/wet risers in good order? | n/a | [5 empty] | 4
32 | [7 empty] | 4
33 | Is fireman's switch working correctly? | n/a | [5 empty] | 4
33 | [7 empty] | 4
Other issues | [7 empty] | 4
34 | Roof void? | Yes | P3 | Roof void survey recommended, access via dwellings, although the pitch is very shallow so may not be appropriate |  |  |  | 5
35 | Other (specify) | [6 empty] | 5
36 | [7 empty] | 5
37 | [7 empty] | 5

## M-M
Priority | Description | Timescale |  |  |  |  | UPRN | G647
P0 | When an unacceptable risk to fire safety is present. Note: Works typically carried out by Housing/Repairs | Within 10 days | [7 empty] | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the Note: RESPONSIVE REPAIRS TEAM | Within 6 months | [7 empty] | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note: PLANNED WORKS TEAM DELIVERY | Within 1 year | [7 empty] | n/k | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years | [7 empty] | n/a | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note: PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years | [8 empty] | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural | [8 empty] | FRA Team
Management and maintenance
Premises: | Tadbourne Court 1-4, HA8 9D |  |  | FRA date: | 2017-02-10
Question | Management/maintenance | Yes/No n/k - n/a | Priority | Location and comment | Details | Ongoing from last FRA? | Completed date
Premises management | [7 empty] | 5
38 | Is there a suitable record of fire safety arrangements available? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  | 5
38 | [7 empty] | 5
39 | Are appropriate fire safety procedures in place? Consider: Emergency action plans; calling/meeting the fire service; ensuring the premises are evacuated; assembly points; assistance for disabled; information to external contractors; nominated staff duties | Yes |  | All responsibilities for fire safety have been addressed with Barnet Homes Fire Safety Policy. The policy is available to all staff on the company intranet. |  |  |  | 5
39 | [7 empty] | 5
40 | Has any liaison taken place with the local fire and rescue service? | Yes |  | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. |  |  |  | 5
40 | [7 empty] | 5
Training | [7 empty] | 5
41 | Do staff receive induction and/or annual fire safety refresher training? | Yes |  | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. |  |  |  | 5
41 | [7 empty] | 5
42 | If drills are considered appropriate, are they carried out at regular intervals? | n/a | [5 empty] | 5
42 | [7 empty] | 5
Maintenance checks | [7 empty] | 5
43 | Are the premises generally well maintained? | Yes |  | The building is generally well maintained with some minor defects that form part of the action plan |  |  |  | 5
43 | [7 empty] | 5
44 | Do appropriate regular checks take place? | Yes |  | Regular checks of the premises are carried out and any defects reported to the building maintenance office. |  |  |  | 5
44 | [7 empty] | 5
45 | Is the alarm system adequately maintained? | n/a | [5 empty] | 5
45 | [7 empty] | 5
46 | Is the escape lighting adequately maintained? | n/k | P4 | Check emergency lighting test records |  |  |  | 6
46 | [7 empty] | 6
47 | Are fire extinguishers adequately maintained? | n/a | [5 empty] | 6
47 | [7 empty] | 6
48 | Are rising mains adequately maintained? | n/a | [5 empty] | 6
48 | [7 empty] | 6
49 | Are fireman lifts adequately maintained? | n/a | [5 empty] | 6
49 | [7 empty] | 6
50 | Is the sprinkler system adequately maintained? | n/a | [5 empty] | 6
50 | [7 empty] | 6
51 | Is the lightning protection system adequately maintained? | Yes |  | A schedule of maintenance is completed by Technical Services under a Service Level Agreement (SLA) |  |  |  | 6
51 | [7 empty] | 6
Records | [7 empty] | 6
52 | Are fire safety maintenance records available for the premises? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  | 6
52 | [7 empty] | 6
53 | Are fire drills recorded? | n/a | [5 empty] | 6
53 | [7 empty] | 6
54 | Is fire safety training recorded? | Yes |  | Records are held centrally by the Health and Safety Team |  |  |  | 6
54 | [7 empty] | 6
55 | Are fire alarm tests recorded? | n/a | [5 empty] | 6
55 | [7 empty] | 6
56 | Are emergency escape lighting tests recorded? | No |  | Not at the premises |  |  |  | 6
56 | [7 empty] | 6
Other issues | [8 empty] | 6
57 | [7 empty] | 6
58 | [7 empty] | 6
59 | [7 empty] | 6
60 | [7 empty] | 6
61 | [7 empty] | 6
62 | [7 empty] | 6

## ActionPlan
| Priority | Description | Timescale |  |  | UPRN |  | No
| P0 | When an unacceptable risk to fire safety is present. Works typically carried out by Housing/Repairs) | Within 10 days |  |  | G647 |  | n/a
| P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the RESPONSIVE REPAIRS TEAM | Within 6 months
| P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year
| P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years
| P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years.
| P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural
FIRE RISK ASSESSMENT ACTION PLAN
| Premises: | Tadbourne Court 1-4, HA8 9D |  |  |  | FRA date: | 2017-02-10
| Question | Action to be taken | Priority | Details | Ongoing from last FRA
1 | 14 | All flat entrance doors (FEDs) in this building are FD30S doors except FED 4 (pic 587) and this door should should be replaced with a certified FD30S door/doorset which should be fitted in accordance to BS8214. | P3
2 | 14 | All pram shed doors are secure, QA check required to confirm fire rating. No significant risk. | P3
3 | 24 | There are call points and sounders in the common areas but no fire alarm panel. A fire alarm system in the common parts of this building is not required and we would recommend a review of the fire strategy for this building, evac plan, etc and if necessary this part of the fire alarm system should be removed. It would be advisable to fit a BS5839-6 LD2 system to all flats if not already fitted. Review recommended. | P3
4 | 27 | It is not known if the building has internal or external stacks. It is recommended that an internal flat survey is carried out to ensure that the compartmentation levels between flats is adequate. | P3
5 | 34 | Roof void survey recommended, access via dwellings, although the pitch is very shallow so may not be appropriate | P3
6 | 46 | Check emergency lighting test records | P4
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63

## Data (hidden)
KeyID | Question | Priority | Location and comment | Ownership | Details | Ongoing from last FRA
0 | 1 | 0 | 0 | #REF! | 0 | 0
0 | 1 | 0 | 0 | #REF! | 0 | 0
0 | 2 | 0 | 0 | #REF! | 0 | 0
0 | 2 | 0 | 0 | #REF! | 0 | 0
0 | 3 | 0 | 0 | #REF! | 0 | 0
0 | 0 | 0 | 0 | #REF! | 0 | 0
0 | 4 | 0 | There is a secure entry system fitted to this building | #REF! | 0 | 0
0 | 4 | 0 | 0 | #REF! | 0 | 0
0 | 5 | 0 | The bins are located in a satisfactory position. | #REF! | 0 | 0
0 | 5 | 0 | 0 | #REF! | 0 | 0
0 | 6 | 0 | No evidence of fire loads near premises. | #REF! | 0 | 0
0 | 6 | 0 | 0 | #REF! | 0 | 0
0 | 0 | 0 | 0 | #REF! | 0 | 0
0 | 7 | 0 | 0 | #REF! | 0 | 0
0 | 7 | 0 | 0 | #REF! | 0 | 0
0 | 0 | 0 | 0 | #REF! | 0 | 0
0 | 8 | 0 | 0 | #REF! | 0 | 0
0 | 8 | 0 | 0 | #REF! | 0 | 0
0 | 0 | 0 | 0 | #REF! | 0 | 0
0 | 9 | 0 | The escape route is satisfactory and meets the requirements of the Building Regulations ADB | #REF! | 0 | 0
0 | 9 | 0 | 0 | #REF! | 0 | 0
0 | 10 | 0 | 0 | #REF! | 0 | 0
0 | 10 | 0 | 0 | #REF! | 0 | 0
0 | 11 | 0 | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. | #REF! | 0 | 0
0 | 11 | 0 | 0 | #REF! | 0 | 0
0 | 12 | 0 | 0 | #REF! | 0 | 0
0 | 12 | 0 | 0 | #REF! | 0 | 0
0 | 13 | 0 | The travel distances are satisfactory and in line with the requirements of the Building Regulations, Approved Document B. | #REF! | 0 | 0
0 | 13 | 0 | 0 | #REF! | 0 | 0
1 | 14 | P3 | All flat entrance doors (FEDs) in this building are FD30S doors except FED 4 (pic 587) and this door should should be replaced with a certified FD30S door/doorset which should be fitted in accordance to BS8214. | #REF! | 0 | 0
1 | 14 | 0 | Electrical intake not located in the common parts | #REF! | 0 | 0
1 | 14 | 0 | 0 | #REF! | 0 | 0
2 | 14 | P3 | All pram shed doors are secure, QA check required to confirm fire rating. No significant risk. | #REF! | 0 | 0
2 | 14 | 0 | 0 | #REF! | 0 | 0
2 | 14 | 0 | 0 | #REF! | 0 | 0
2 | 14 | 0 | 0 | #REF! | 0 | 0
2 | 14 | 0 | 0 | #REF! | 0 | 0
2 | 14 | 0 | 0 | #REF! | 0 | 0
2 | 14 | 0 | 0 | #REF! | 0 | 0
2 | 15 | 0 | 0 | #REF! | 0 | 0
2 | 15 | 0 | 0 | #REF! | 0 | 0
2 | 16 | 0 | All escape routes lead to open air at ground level. | #REF! | 0 | 0
2 | 16 | 0 | 0 | #REF! | 0 | 0
2 | 17 | 0 | 0 | #REF! | 0 | 0
2 | 17 | 0 | 0 | #REF! | 0 | 0
2 | 18 | 0 | Every stair nosing needs to be highlighted internally & externally with a minimum of a 25mm strip across the full length of the front part of the step. Consideration should be given to fitting Photoluminescent nosings/strips in accordance to BS5266-6 as well or to HSE guidleines relating to slips, trips and falls particularly as staircases are the main means of escape for persons on the first floor or higher in any building. Existing nosings are highlighted with appropriate photoluminescent nosings | #REF! | 0 | 0
2 | 18 | 0 | 0 | #REF! | 0 | 0
2 | 19 | 0 | All stair nosings should be easily identifiable to visually impaired and blind persons as a matter of duty of care and should achieve the Light Reflectance Values as set out in ADM (a LRV of 30) particularly as these staircases are the main means of escape in the event of fire (for persons on the 1st floor). | #REF! | 0 | 0
2 | 19 | 0 | 0 | #REF! | 0 | 0
2 | 0 | 0 | 0 | #REF! | 0 | 0
2 | 20 | 0 | There is emergency lighting fitted in this building, it has not been fitted to standard but it is not required | #REF! | 0 | 0
2 | 20 | 0 | 0 | #REF! | 0 | 0
2 | 21 | 0 | 0 | #REF! | 0 | 0
2 | 21 | 0 | 0 | #REF! | 0 | 0
2 | 0 | 0 | 0 | #REF! | 0 | 0
2 | 22 | 0 | 0 | #REF! | 0 | 0
2 | 22 | 0 | 0 | #REF! | 0 | 0
2 | 22 | 0 | 0 | #REF! | 0 | 0
2 | 22 | 0 | 0 | #REF! | 0 | 0
2 | 22 | 0 | 0 | #REF! | 0 | 0
2 | 22 | 0 | 0 | #REF! | 0 | 0
2 | 23 | 0 | 0 | #REF! | 0 | 0
2 | 23 | 0 | 0 | #REF! | 0 | 0
2 | 0 | 0 | 0 | #REF! | 0 | 0
3 | 24 | P3 | There are call points and sounders in the common areas but no fire alarm panel. A fire alarm system in the common parts of this building is not required and we would recommend a review of the fire strategy for this building, evac plan, etc and if necessary this part of the fire alarm system should be removed. It would be advisable to fit a BS5839-6 LD2 system to all flats if not already fitted. Review recommended. | #REF! | 0 | 0
3 | 24 | 0 | 0 | #REF! | 0 | 0
3 | 25 | 0 | 0 | #REF! | 0 | 0
3 | 25 | 0 | 0 | #REF! | 0 | 0
3 | 26 | 0 | 0 | #REF! | 0 | 0
3 | 26 | 0 | 0 | #REF! | 0 | 0
3 | 0 | 0 | 0 | #REF! | 0 | 0
4 | 27 | P3 | It is not known if the building has internal or external stacks. It is recommended that an internal flat survey is carried out to ensure that the compartmentation levels between flats is adequate. | #REF! | 0 | 0
4 | 27 | 0 | 0 | #REF! | 0 | 0
4 | 27 | 0 | 0 | #REF! | 0 | 0
4 | 27 | 0 | 0 | #REF! | 0 | 0
4 | 27 | 0 | 0 | #REF! | 0 | 0
4 | 28 | 0 | 0 | #REF! | 0 | 0
4 | 28 | 0 | 0 | #REF! | 0 | 0
4 | 29 | 0 | 0 | #REF! | 0 | 0
4 | 29 | 0 | 0 | #REF! | 0 | 0
4 | 0 | 0 | 0 | #REF! | 0 | 0
4 | 30 | 0 | The communal areas should be sterile areas and as such it is considered that fire extinguishers are not required. It should be noted that fire extinguishers can pose a risk to life if used by untrained people. | #REF! | 0 | 0
4 | 30 | 0 | 0 | #REF! | 0 | 0
4 | 31 | 0 | 0 | #REF! | 0 | 0
4 | 31 | 0 | 0 | #REF! | 0 | 0
4 | 32 | 0 | 0 | #REF! | 0 | 0
4 | 32 | 0 | 0 | #REF! | 0 | 0
4 | 33 | 0 | 0 | #REF! | 0 | 0
4 | 33 | 0 | 0 | #REF! | 0 | 0
4 | 0 | 0 | 0 | #REF! | 0 | 0
5 | 34 | P3 | Roof void survey recommended, access via dwellings, although the pitch is very shallow so may not be appropriate | #REF! | 0 | 0
5 | 35 | 0 | 0 | #REF! | 0 | 0
5 | 36 | 0 | 0 | #REF! | 0 | 0
5 | 37 | 0 | 0 | #REF! | 0 | 0
5 | 38 | 0 | Records are held centrally by the Health and Safety Team | #REF! | 0 | 0
5 | 38 | 0 | 0 | #REF! | 0 | 0
5 | 39 | 0 | All responsibilities for fire safety have been addressed with Barnet Homes Fire Safety Policy. The policy is available to all staff on the company intranet. | #REF! | 0 | 0
5 | 39 | 0 | 0 | #REF! | 0 | 0
5 | 40 | 0 | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. | #REF! | 0 | 0
5 | 40 | 0 | 0 | #REF! | 0 | 0
5 | 0 | 0 | 0 | #REF! | 0 | 0
5 | 41 | 0 | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. | #REF! | 0 | 0
5 | 41 | 0 | 0 | #REF! | 0 | 0
5 | 42 | 0 | 0 | #REF! | 0 | 0
5 | 42 | 0 | 0 | #REF! | 0 | 0
5 | 0 | 0 | 0 | #REF! | 0 | 0
5 | 43 | 0 | The building is generally well maintained with some minor defects that form part of the action plan | #REF! | 0 | 0
5 | 43 | 0 | 0 | #REF! | 0 | 0
5 | 44 | 0 | Regular checks of the premises are carried out and any defects reported to the building maintenance office. | #REF! | 0 | 0
5 | 44 | 0 | 0 | #REF! | 0 | 0
5 | 45 | 0 | 0 | #REF! | 0 | 0
5 | 45 | 0 | 0 | #REF! | 0 | 0
6 | 46 | P4 | Check emergency lighting test records | #REF! | 0 | 0
6 | 46 | 0 | 0 | #REF! | 0 | 0
6 | 47 | 0 | 0 | #REF! | 0 | 0
6 | 47 | 0 | 0 | #REF! | 0 | 0
6 | 48 | 0 | 0 | #REF! | 0 | 0
6 | 48 | 0 | 0 | #REF! | 0 | 0
6 | 49 | 0 | 0 | #REF! | 0 | 0
6 | 49 | 0 | 0 | #REF! | 0 | 0
6 | 50 | 0 | 0 | #REF! | 0 | 0
6 | 50 | 0 | 0 | #REF! | 0 | 0
6 | 51 | 0 | A schedule of maintenance is completed by Technical Services under a Service Level Agreement (SLA) | #REF! | 0 | 0
6 | 51 | 0 | 0 | #REF! | 0 | 0
6 | 0 | 0 | 0 | #REF! | 0 | 0
6 | 52 | 0 | Records are held centrally by the Health and Safety Team | #REF! | 0 | 0
6 | 52 | 0 | 0 | #REF! | 0 | 0
6 | 53 | 0 | 0 | #REF! | 0 | 0
6 | 53 | 0 | 0 | #REF! | 0 | 0
6 | 54 | 0 | Records are held centrally by the Health and Safety Team | #REF! | 0 | 0
6 | 54 | 0 | 0 | #REF! | 0 | 0
6 | 55 | 0 | 0 | #REF! | 0 | 0
6 | 55 | 0 | 0 | #REF! | 0 | 0
6 | 56 | 0 | Not at the premises | #REF! | 0 | 0
6 | 56 | 0 | 0 | #REF! | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0
6 | 57 | 0 | 0 | #REF! | 0 | 0
6 | 58 | 0 | 0 | #REF! | 0 | 0
6 | 59 | 0 | 0 | #REF! | 0 | 0
6 | 60 | 0 | 0 | #REF! | 0 | 0
6 | 61 | 0 | 0 | #REF! | 0 | 0
6 | 62 | 0 | 0 | #REF! | 0 | 0